## Sheet1(DE)
Kategorie | Sortierung (Kategorie) | Addresse | Typ | Zugriffsrecht | Beschreibung | Einheit | Min | Max
Häufig benötigte Messwerte | 1 | 19000 | float | RD | Voltage L1-N | V
Häufig benötigte Messwerte | 1 | 19002 | float | RD | Voltage L2-N | V
Häufig benötigte Messwerte | 1 | 19004 | float | RD | Voltage L3-N | V
Häufig benötigte Messwerte | 1 | 19006 | float | RD | Voltage L1-L2 | V
Häufig benötigte Messwerte | 1 | 19008 | float | RD | Voltage L2-L3 | V
Häufig benötigte Messwerte | 1 | 19010 | float | RD | Voltage L3-L1 | V
Häufig benötigte Messwerte | 1 | 19012 | float | RD | Current, L1 | A
Häufig benötigte Messwerte | 1 | 19014 | float | RD | Current, L2 | A
Häufig benötigte Messwerte | 1 | 19016 | float | RD | Current, L3 | A
Häufig benötigte Messwerte | 1 | 19018 | float | RD | Vector sum, IN=I1+I2+I3 | A
Häufig benötigte Messwerte | 1 | 19020 | float | RD | Real power L1 | W
Häufig benötigte Messwerte | 1 | 19022 | float | RD | Real power L2 | W
Häufig benötigte Messwerte | 1 | 19024 | float | RD | Real power L3 | W
Häufig benötigte Messwerte | 1 | 19026 | float | RD | Sum, Psum3=P1+P2+P3 | W
Häufig benötigte Messwerte | 1 | 19028 | float | RD | Apparent power L1 | VA
Häufig benötigte Messwerte | 1 | 19030 | float | RD | Apparent power L2 | VA
Häufig benötigte Messwerte | 1 | 19032 | float | RD | Apparent power L3 | VA
Häufig benötigte Messwerte | 1 | 19034 | float | RD | Sum, Ssum3=S1+S2+S3 | VA
Häufig benötigte Messwerte | 1 | 19036 | float | RD | Reactive power (mains frequ.) L1 | var
Häufig benötigte Messwerte | 1 | 19038 | float | RD | Reactive power (mains frequ.) L2 | var
Häufig benötigte Messwerte | 1 | 19040 | float | RD | Reactive power (mains frequ.) L3 | var
Häufig benötigte Messwerte | 1 | 19042 | float | RD | Sum, Qsum3=Q1+Q2+Q3 | var
Häufig benötigte Messwerte | 1 | 19044 | float | RD | Power factor fundamental oscill., Cos(ϕ), UL1 IL1
Häufig benötigte Messwerte | 1 | 19046 | float | RD | Power factor fundamental oscill., Cos(ϕ),, UL2 IL2
Häufig benötigte Messwerte | 1 | 19048 | float | RD | Power factor fundamental oscill., Cos(ϕ),, UL3 IL3
Häufig benötigte Messwerte | 1 | 19050 | float | RD | Measured frequency | Hz
Häufig benötigte Messwerte | 1 | 19052 | float | RD | Rotation field, 1=right, 0=none, -1=left
Häufig benötigte Messwerte | 1 | 19054 | float | RD | Real energy L1, consumed | Wh
Häufig benötigte Messwerte | 1 | 19056 | float | RD | Real energy L2, consumed | Wh
Häufig benötigte Messwerte | 1 | 19058 | float | RD | Real energy L3, consumed | Wh
Häufig benötigte Messwerte | 1 | 19060 | float | RD | Real energy L1..L3 | Wh
Häufig benötigte Messwerte | 1 | 19062 | float | RD | Real energy L1, consumed | Wh
Häufig benötigte Messwerte | 1 | 19064 | float | RD | Real energy L2, consumed | Wh
Häufig benötigte Messwerte | 1 | 19066 | float | RD | Real energy L3, consumed | Wh
Häufig benötigte Messwerte | 1 | 19068 | float | RD | Real energy L1..L3, consumed, rate 1 | Wh
Häufig benötigte Messwerte | 1 | 19070 | float | RD | Real energy L1, delivered | Wh
Häufig benötigte Messwerte | 1 | 19072 | float | RD | Real energy L2, delivered | Wh
Häufig benötigte Messwerte | 1 | 19074 | float | RD | Real energy L3, delivered | Wh
Häufig benötigte Messwerte | 1 | 19076 | float | RD | Real energy L1..L3, delivered | Wh
Häufig benötigte Messwerte | 1 | 19078 | float | RD | Apparent energy L1 | VAh
Häufig benötigte Messwerte | 1 | 19080 | float | RD | Apparent energy L2 | VAh
Häufig benötigte Messwerte | 1 | 19082 | float | RD | Apparent energy L3 | VAh
Häufig benötigte Messwerte | 1 | 19084 | float | RD | Apparent energy L1..L3 | VAh
Häufig benötigte Messwerte | 1 | 19086 | float | RD | Reactive energy, inductive, L1 | varh
Häufig benötigte Messwerte | 1 | 19088 | float | RD | Reactive energy, inductive, L2 | varh
Häufig benötigte Messwerte | 1 | 19090 | float | RD | Reactive energy, inductive, L3 | varh
Häufig benötigte Messwerte | 1 | 19092 | float | RD | Reactive energy L1..L3 | varh
Häufig benötigte Messwerte | 1 | 19094 | float | RD | Reactive energy, inductive, L1 | varh
Häufig benötigte Messwerte | 1 | 19096 | float | RD | Reactive energy, inductive, L2 | varh
Häufig benötigte Messwerte | 1 | 19098 | float | RD | Reactive energy, inductive, L3 | varh
Häufig benötigte Messwerte | 1 | 19100 | float | RD | Reactive energy L1..L3, ind. | varh
Häufig benötigte Messwerte | 1 | 19102 | float | RD | Reactive energy, capacitive, L1 | varh
Häufig benötigte Messwerte | 1 | 19104 | float | RD | Reactive energy, capacitive, L2 | varh
Häufig benötigte Messwerte | 1 | 19106 | float | RD | Reactive energy, capacitive, L3 | varh
Häufig benötigte Messwerte | 1 | 19108 | float | RD | Reactive energy L1..L3, cap. | varh
Häufig benötigte Messwerte | 1 | 19110 | float | RD | Harmonic, THD,U L1-N | %
Häufig benötigte Messwerte | 1 | 19112 | float | RD | Harmonic, THD,U L2-N | %
Häufig benötigte Messwerte | 1 | 19114 | float | RD | Harmonic, THD,U L3-N | %
Häufig benötigte Messwerte | 1 | 19116 | float | RD | Harmonic, THD,I L1 | %
Häufig benötigte Messwerte | 1 | 19118 | float | RD | Harmonic, THD,I L2 | %
Häufig benötigte Messwerte | 1 | 19120 | float | RD | Harmonic, THD,I L3 | %
Messwerte | 2 | 991 | float | RD | Measured value (float): current max value for current RMS of all 3 phases | A
Messwerte | 2 | 993 | ushort | RD | Measured value (float): the corresponding phase number (1...3)
Messwerte | 2 | 1000 | float | RD | Measured value (float): voltage L1-N | V
Messwerte | 2 | 1002 | float | RD | Measured value (float): voltage L2-N | V
Messwerte | 2 | 1004 | float | RD | Measured value (float): voltage L3-N | V
Messwerte | 2 | 1006 | float | RD | Measured value (float): voltage L1-L2 | V
Messwerte | 2 | 1008 | float | RD | Measured value (float): voltage L2-L3 | V
Messwerte | 2 | 1010 | float | RD | Measured value (float): voltage L3-L1 | V
Messwerte | 2 | 1012 | float | RD | Measured value (float): current L1 | A
Messwerte | 2 | 1014 | float | RD | Measured value (float): current L2 | A
Messwerte | 2 | 1016 | float | RD | Measured value (float): current L3 | A
Messwerte | 2 | 1018 | float | RD | Measured value (float): current sum (calculated current in N) | A
Messwerte | 2 | 1020 | float | RD | Measured value (float): active power L1 | W
Messwerte | 2 | 1022 | float | RD | Measured value (float): active power L2 | W
Messwerte | 2 | 1024 | float | RD | Measured value (float): active power L3 | W
Messwerte | 2 | 1026 | float | RD | Measured value (float): active power sum | W
Messwerte | 2 | 1028 | float | RD | Measured value (float): reactive power L1 | var
Messwerte | 2 | 1030 | float | RD | Measured value (float): reactive power L2 | var
Messwerte | 2 | 1032 | float | RD | Measured value (float): reactive power L3 | var
Messwerte | 2 | 1034 | float | RD | Measured value (float): reactive power sum | var
Messwerte | 2 | 1036 | float | RD | Measured value (float): apparent power L1 | VA
Messwerte | 2 | 1038 | float | RD | Measured value (float): apparent power L2 | VA
Messwerte | 2 | 1040 | float | RD | Measured value (float): apparent power L3 | VA
Messwerte | 2 | 1042 | float | RD | Measured value (float): apparent power sum | VA
Messwerte | 2 | 1044 | float | RD | Measured value (float): cos(ϕ) L1
Messwerte | 2 | 1046 | float | RD | Measured value (float): cos(ϕ) L2
Messwerte | 2 | 1048 | float | RD | Measured value (float): cos(ϕ) L3
Messwerte | 2 | 1050 | float | RD | Measured value (float): cos(ϕ) sum
Messwerte | 2 | 1052 | float | RD | Measured value (float): active power of the fundamental oscillation L1 | W
Messwerte | 2 | 1054 | float | RD | Measured value (float): active power of the fundamental oscillation L2 | W
Messwerte | 2 | 1056 | float | RD | Measured value (float): active power of the fundamental oscillation L3 | W
Messwerte | 2 | 1214 | float | RD | Measured value (float): THD voltage L1 [%] | %
Messwerte | 2 | 1216 | float | RD | Measured value (float): THD voltage L2 [%] | %
Messwerte | 2 | 1218 | float | RD | Measured value (float): THD voltage L3 [%] | %
Messwerte | 2 | 1220 | float | RD | Measured value (float): THD current L1 [%] | %
Messwerte | 2 | 1222 | float | RD | Measured value (float): THD current L1 [%] | %
Messwerte | 2 | 1224 | float | RD | Measured value (float): THD current L1 [%] | %
Messwerte | 2 | 1226 | float | RD | Measured value (float): frequency | Hz
Messwerte | 2 | 1228 | float | RD | Measured value (float): zero sequence voltage
Messwerte | 2 | 1230 | float | RD | Measured value (float): positive sequence voltage
Messwerte | 2 | 1232 | float | RD | Measured value (float): negative sequence voltage
Messwerte | 2 | 1234 | float | RD | Measured value (float): zero sequence current
Messwerte | 2 | 1236 | float | RD | Measured value (float): positive sequence current
Messwerte | 2 | 1238 | float | RD | Measured value (float): negative sequence current
Messwerte | 2 | 1240 | float | RD | Measured value (float): distortion power L1 | var
Messwerte | 2 | 1242 | float | RD | Measured value (float): distortion power L2 | var
Messwerte | 2 | 1244 | float | RD | Measured value (float): distortion power L3 | var
Messwerte | 2 | 1246 | float | RD | Measured value (float): distortion power sum | var
Messwerte | 2 | 1248 | float | RD | Measured value (float): Rotation field, 1=right, 0=none, -1=left
Messwerte | 2 | 1250 | float | RD | Measured value (float): real part of the fundamental oscillation voltage L1 | V
Messwerte | 2 | 1252 | float | RD | Measured value (float): imaginary part of the fundamental oscillation voltage L1 | V
Messwerte | 2 | 1254 | float | RD | Measured value (float): real part of the fundamental oscillation voltage L2 | V
Messwerte | 2 | 1256 | float | RD | Measured value (float): imaginary part of the fundamental oscillation voltage L2 | V
Messwerte | 2 | 1258 | float | RD | Measured value (float): real part of the fundamental oscillation voltage L3 | V
Messwerte | 2 | 1260 | float | RD | Measured value (float): imaginary part of the fundamental oscillation voltage L3 | V
Messwerte | 2 | 1262 | float | RD | Measured value (float): real part of the fundamental oscillation current L1 | A
Messwerte | 2 | 1264 | float | RD | Measured value (float): imaginary part of the fundamental oscillation current L1 | A
Messwerte | 2 | 1266 | float | RD | Measured value (float): real part of the fundamental oscillation current L2 | A
Messwerte | 2 | 1268 | float | RD | Measured value (float): imaginary part of the fundamental oscillation current L2 | A
Messwerte | 2 | 1270 | float | RD | Measured value (float): real part of the fundamental oscillation current L3 | A
Messwerte | 2 | 1272 | float | RD | Measured value (float): imaginary part of the fundamental oscillation current L3 | A
Messwerte | 2 | 1274 | float | RD | Measured value (float): frequency (200ms) | Hz
Messwerte | 2 | 1276 | float | RD | Measured value (float): TDD (total demand distortion) current L1 | %
Messwerte | 2 | 1278 | float | RD | Measured value (float): TDD (total demand distortion) current L2 | %
Messwerte | 2 | 1280 | float | RD | Measured value (float): TDD (total demand distortion) current L3 | %
Messwerte | 2 | 1282 | float | RD | Measured value (float): crest factor voltageL1
Messwerte | 2 | 1284 | float | RD | Measured value (float): crest factor voltageL2
Messwerte | 2 | 1286 | float | RD | Measured value (float): crest factor voltageL3
Messwerte | 2 | 1288 | float | RD | Measured value (float): crest factor current L1
Messwerte | 2 | 1290 | float | RD | Measured value (float): crest factor current L2
Messwerte | 2 | 1292 | float | RD | Measured value (float): crest factor current L3
Messwerte | 2 | 1294 | float | RD | Measured value (float): power factor L1
Messwerte | 2 | 1296 | float | RD | Measured value (float): power factor L2
Messwerte | 2 | 1298 | float | RD | Measured value (float): power factor L3
Messwerte | 2 | 1300 | float | RD | Measured value (float): power factor sum3=Psum3/Ssum3
Messwerte | 2 | 1329 | float | RD | Measured value (float): voltage asymmetry [%] | %
Messwerte | 2 | 1331 | float | RD | Measured value (float): current asymmetry [%] | %
Messwerte | 2 | 1400 | float | RD | Angular shift of the current I1 in the unit circle, relative to normal zero | deg
Messwerte | 2 | 1402 | float | RD | Angular shift of the current I2 in the unit circle, relative to normal zero | deg
Messwerte | 2 | 1404 | float | RD | Angular shift of the current I3 in the unit circle, relative to normal zero | deg
Messwerte | 2 | 11000 | short (x10) | RD | Measured value (short): voltage L1-N | V
Messwerte | 2 | 11001 | short (x10) | RD | Measured value (short): voltage L2-N | V
Messwerte | 2 | 11002 | short (x10) | RD | Measured value (short): voltage L3-N | V
Messwerte | 2 | 11003 | short (x10) | RD | Measured value (short): voltage L1-L2 | V
Messwerte | 2 | 11004 | short (x10) | RD | Measured value (short): voltage L2-L3 | V
Messwerte | 2 | 11005 | short (x10) | RD | Measured value (short): voltage L3-L1 | V
Messwerte | 2 | 11006 | short (x1000) | RD | Measured value (short): current L1 | A
Messwerte | 2 | 11007 | short (x1000) | RD | Measured value (short): current L2 | A
Messwerte | 2 | 11008 | short (x1000) | RD | Measured value (short): current L3 | A
Messwerte | 2 | 11009 | short (x1000) | RD | Measured value (short): current sum | A
Messwerte | 2 | 11010 | short (x10) | RD | Measured value (short): active power L1 | W
Messwerte | 2 | 11011 | short (x10) | RD | Measured value (short): active power L2 | W
Messwerte | 2 | 11012 | short (x10) | RD | Measured value (short): active power L3 | W
Messwerte | 2 | 11013 | short | RD | Measured value (short): active power sum | W
Messwerte | 2 | 11014 | short (x10) | RD | Measured value (short): reactive power L1 | var
Messwerte | 2 | 11015 | short (x10) | RD | Measured value (short): reactive power L2 | var
Messwerte | 2 | 11016 | short (x10) | RD | Measured value (short): reactive power L3 | var
Messwerte | 2 | 11017 | short | RD | Measured value (short): reactive power sum | var
Messwerte | 2 | 11018 | short (x10) | RD | Measured value (short): apparent power L1 | VA
Messwerte | 2 | 11019 | short (x10) | RD | Measured value (short): apparent power L2 | VA
Messwerte | 2 | 11020 | short (x10) | RD | Measured value (short): apparent power L3 | VA
Messwerte | 2 | 11021 | short | RD | Measured value (short): apparent power sum | VA
Messwerte | 2 | 11022 | short (x100) | RD | Measured value (short): cos(ϕ) L1
Messwerte | 2 | 11023 | short (x100) | RD | Measured value (short): cos(ϕ) L2
Messwerte | 2 | 11024 | short (x100) | RD | Measured value (short): cos(ϕ) L3
Messwerte | 2 | 11025 | short (x100) | RD | Measured value (short): cos(ϕ) sum
Messwerte | 2 | 11026 | short (x10) | RD | Measured value (short): active power fundamental oscillation L1 | W
Messwerte | 2 | 11027 | short (x10) | RD | Measured value (short): active power fundamental oscillation L2 | W
Messwerte | 2 | 11028 | short (x10) | RD | Measured value (short): active power fundamental oscillation L3 | W
Messwerte | 2 | 11111 | short (x100) | RD | Measured value (short): THD voltage L1-N [%] | %
Messwerte | 2 | 11112 | short (x100) | RD | Measured value (short): THD voltage L2-N [%] | %
Messwerte | 2 | 11113 | short (x100) | RD | Measured value (short): THD voltage L3-N [%] | %
Messwerte | 2 | 11114 | short (x100) | RD | Measured value (short): THD current L1 [%] | %
Messwerte | 2 | 11115 | short (x100) | RD | Measured value (short): THD current L2 [%] | %
Messwerte | 2 | 11116 | short (x100) | RD | Measured value (short): THD current L3 [%] | %
Messwerte | 2 | 11117 | short (x10) | RD | Measured value (short): frequency | Hz
Messwerte | 2 | 11118 | short (x10) | RD | Measured value (short): zero sequence voltage
Messwerte | 2 | 11119 | short (x10) | RD | Measured value (short): positive sequence voltage
Messwerte | 2 | 11120 | short (x10) | RD | Measured value (short): negative sequence voltage
Messwerte | 2 | 11121 | short (x1000) | RD | Measured value (short): zero sequence current
Messwerte | 2 | 11122 | short (x1000) | RD | Measured value (short): positive sequence current
Messwerte | 2 | 11123 | short (x1000) | RD | Measured value (short): negative sequence current
Messwerte | 2 | 11124 | short (x10) | RD | Measured value (short): distortion power L1 | var
Messwerte | 2 | 11125 | short (x10) | RD | Measured value (short): distortion power L2 | var
Messwerte | 2 | 11126 | short (x10) | RD | Measured value (short): distortion power L3 | var
Messwerte | 2 | 11127 | short | RD | Measured value (short): distortion power sum | var
Messwerte | 2 | 11128 | short (x10) | RD | Measured value (short): Rotation field: > 0 = right, 0 = none, < 0 = left
Messwerte | 2 | 11168 | ushort (x1000) | RD | Measured value (short): crest factor voltage L1-N
Messwerte | 2 | 11169 | ushort (x1000) | RD | Measured value (short): crest factor voltage L2-N
Messwerte | 2 | 11170 | ushort (x1000) | RD | Measured value (short): crest factor voltage L3-N
Messwerte | 2 | 11171 | ushort (x1000) | RD | Measured value (short): crest factor current L1
Messwerte | 2 | 11172 | ushort (x1000) | RD | Measured value (short): crest factor current L2
Messwerte | 2 | 11173 | ushort (x1000) | RD | Measured value (short): crest factor current L3
Maximalwerte | 4 | 3000 | float | RD | Maximum value (float): voltage L1-N | V
Maximalwerte | 4 | 3002 | float | RD | Maximum value (float): voltage L2-N | V
Maximalwerte | 4 | 3004 | float | RD | Maximum value (float): voltage L3-N | V
Maximalwerte | 4 | 3006 | float | RD | Maximum value (float): voltage L1-L2 | V
Maximalwerte | 4 | 3008 | float | RD | Maximum value (float): voltage L2-L3 | V
Maximalwerte | 4 | 3010 | float | RD | Maximum value (float): voltage L3-L1 | V
Maximalwerte | 4 | 3012 | float | RD | Maximum value (float): current L1 | A
Maximalwerte | 4 | 3014 | float | RD | Maximum value (float): current L2 | A
Maximalwerte | 4 | 3016 | float | RD | Maximum value (float): current L3 | A
Maximalwerte | 4 | 3018 | float | RD | Maximum value (float): current sum | A
Maximalwerte | 4 | 3020 | float | RD | Maximum value (float): active power L1 | W
Maximalwerte | 4 | 3022 | float | RD | Maximum value (float): active power L2 | W
Maximalwerte | 4 | 3024 | float | RD | Maximum value (float): active power L3 | W
Maximalwerte | 4 | 3026 | float | RD | Maximum value (float): active power sum | W
Maximalwerte | 4 | 3028 | float | RD | Maximum value (float): reactive power L1 | var
Maximalwerte | 4 | 3030 | float | RD | Maximum value (float): reactive power L2 | var
Maximalwerte | 4 | 3032 | float | RD | Maximum value (float): reactive power L3 | var
Maximalwerte | 4 | 3034 | float | RD | Maximum value (float): reactive power sum | var
Maximalwerte | 4 | 3036 | float | RD | Maximum value (float): apparent power L1 | VA
Maximalwerte | 4 | 3038 | float | RD | Maximum value (float): apparent power L2 | VA
Maximalwerte | 4 | 3040 | float | RD | Maximum value (float): apparent power L3 | VA
Maximalwerte | 4 | 3042 | float | RD | Maximum value (float): apparent power sum | VA
Maximalwerte | 4 | 3044 | float | RD | Maximum value (float): cos(ϕ) L1
Maximalwerte | 4 | 3046 | float | RD | Maximum value (float): cos(ϕ) L2
Maximalwerte | 4 | 3048 | float | RD | Maximum value (float): cos(ϕ) L3
Maximalwerte | 4 | 3050 | float | RD | Maximum value (float): cos(ϕ) sum
Maximalwerte | 4 | 3052 | float | RD | Maximum value (float): active power, fundamental oscillation L1 | V
Maximalwerte | 4 | 3054 | float | RD | Maximum value (float): active power, fundamental oscillation L2 | V
Maximalwerte | 4 | 3056 | float | RD | Maximum value (float): active power, fundamental oscillation L3 | V
Maximalwerte | 4 | 3214 | float | RD | Maximum value (float): THD voltage L1 | %
Maximalwerte | 4 | 3216 | float | RD | Maximum value (float): THD voltage L2 | %
Maximalwerte | 4 | 3218 | float | RD | Maximum value (float): THD voltage L3 | %
Maximalwerte | 4 | 3220 | float | RD | Maximum value (float): THD current L1 | %
Maximalwerte | 4 | 3222 | float | RD | Maximum value (float): THD current L2 | %
Maximalwerte | 4 | 3224 | float | RD | Maximum value (float): THD current L3 | %
Maximalwerte | 4 | 3226 | float | RD | Maximum value (float): frequency | Hz
Maximalwerte | 4 | 3228 | float | RD | Maximum value (float): voltage zero sequence
Maximalwerte | 4 | 3230 | float | RD | Maximum value (float): voltage positive sequence
Maximalwerte | 4 | 3232 | float | RD | Maximum value (float): voltage negative sequence
Maximalwerte | 4 | 3234 | float | RD | Maximum value (float): current zero sequence
Maximalwerte | 4 | 3236 | float | RD | Maximum value (float): current positive sequence
Maximalwerte | 4 | 3238 | float | RD | Maximum value (float): current negative sequence
Maximalwerte | 4 | 3240 | float | RD | Maximum value (float): distortion power L1 | var
Maximalwerte | 4 | 3242 | float | RD | Maximum value (float): distortion power L2 | var
Maximalwerte | 4 | 3244 | float | RD | Maximum value (float): distortion power L3 | var
Maximalwerte | 4 | 3246 | float | RD | Maximum value (float): distortion power sum | var
Maximalwerte | 4 | 3264 | float | RD | Maximum value (float): TDD current L1 [%] | %
Maximalwerte | 4 | 3266 | float | RD | Maximum value (float): TDD current L2 [%] | %
Maximalwerte | 4 | 3268 | float | RD | Maximum value (float): TDD current L3 [%] | %
Maximalwerte | 4 | 3270 | float | RD | Maximum value (float): max. value power factor L1
Maximalwerte | 4 | 3272 | float | RD | Maximum value (float): max. value power factor L2
Maximalwerte | 4 | 3274 | float | RD | Maximum value (float): max. value power factor L3
Maximalwerte | 4 | 3276 | float | RD | Maximum value (float): max. value power factor sum3=Psum3/Ssum3
Maximalwerte | 4 | 3278 | float | RD | Maximum value (float): voltage asymmetry [%] (max) | %
Maximalwerte | 4 | 3280 | float | RD | Maximum value (float): current asymmetry [%] (max) | %
Maximalwerte | 4 | 13000 | short (x10) | RD | Maximum value (short): voltage L1-N | V
Maximalwerte | 4 | 13001 | short (x10) | RD | Maximum value (short): voltage L2-N | V
Maximalwerte | 4 | 13002 | short (x10) | RD | Maximum value (short): voltage L3-N | V
Maximalwerte | 4 | 13003 | short (x10) | RD | Maximum value (short): voltage L1-L2 | V
Maximalwerte | 4 | 13004 | short (x10) | RD | Maximum value (short): voltage L2-L3 | V
Maximalwerte | 4 | 13005 | short (x10) | RD | Maximum value (short): voltage L3-L1 | V
Maximalwerte | 4 | 13006 | short (x1000) | RD | Maximum value (short): current L1 | A
Maximalwerte | 4 | 13007 | short (x1000) | RD | Maximum value (short): current L2 | A
Maximalwerte | 4 | 13008 | short (x1000) | RD | Maximum value (short): current L3 | A
Maximalwerte | 4 | 13009 | short (x1000) | RD | Maximum value (short): current sum | A
Maximalwerte | 4 | 13010 | short (x10) | RD | Maximum value (short): active power L1 | W
Maximalwerte | 4 | 13011 | short (x10) | RD | Maximum value (short): active power L2 | W
Maximalwerte | 4 | 13012 | short (x10) | RD | Maximum value (short): active power L3 | W
Maximalwerte | 4 | 13013 | short | RD | Maximum value (short): active power sum | W
Maximalwerte | 4 | 13014 | short (x10) | RD | Maximum value (short): reactive power L1 | var
Maximalwerte | 4 | 13015 | short (x10) | RD | Maximum value (short): reactive power L2 | var
Maximalwerte | 4 | 13016 | short (x10) | RD | Maximum value (short): reactive power L3 | var
Maximalwerte | 4 | 13017 | short | RD | Maximum value (short): reactive power sum | var
Maximalwerte | 4 | 13018 | short (x10) | RD | Maximum value (short): apparent power L1 | VA
Maximalwerte | 4 | 13019 | short (x10) | RD | Maximum value (short): apparent power L2 | VA
Maximalwerte | 4 | 13020 | short (x10) | RD | Maximum value (short): apparent power L3 | VA
Maximalwerte | 4 | 13021 | short | RD | Maximum value (short): apparent power sum | VA
Maximalwerte | 4 | 13022 | short (x1000) | RD | Maximum value (short): cos(ϕ) L1
Maximalwerte | 4 | 13023 | short (x1000) | RD | Maximum value (short): cos(ϕ) L2
Maximalwerte | 4 | 13024 | short (x1000) | RD | Maximum value (short): cos(ϕ) L3
Maximalwerte | 4 | 13025 | short (x1000) | RD | Maximum value (short): cos(ϕ) sum
Maximalwerte | 4 | 13026 | short (x10) | RD | Maximum value (short): active power of fundamental oscillation L1 | W
Maximalwerte | 4 | 13027 | short (x10) | RD | Maximum value (short): active power of fundamental oscillation L2 | W
Maximalwerte | 4 | 13028 | short (x10) | RD | Maximum value (short): active power of fundamental oscillation L3 | W
Maximalwerte | 4 | 13107 | short (x100) | RD | Maximum value (short): THD voltage L1 | %
Maximalwerte | 4 | 13108 | short (x100) | RD | Maximum value (short): THD voltage L2 | %
Maximalwerte | 4 | 13109 | short (x100) | RD | Maximum value (short): THD voltage L3 | %
Maximalwerte | 4 | 13110 | short (x100) | RD | Maximum value (short): THD current L1 | %
Maximalwerte | 4 | 13111 | short (x100) | RD | Maximum value (short): THD current L2 | %
Maximalwerte | 4 | 13112 | short (x100) | RD | Maximum value (short): THD current L3 | %
Maximalwerte | 4 | 13113 | short (x100) | RD | Maximum value (short): frequency
Maximalwerte | 4 | 13114 | short (x10) | RD | Maximum value (short): voltage zero sequence
Maximalwerte | 4 | 13115 | short (x10) | RD | Maximum value (short): voltage positive sequence
Maximalwerte | 4 | 13116 | short (x10) | RD | Maximum value (short): voltage negative sequence
Maximalwerte | 4 | 13117 | short (x1000) | RD | Maximum value (short): current zero sequence
Maximalwerte | 4 | 13118 | short (x1000) | RD | Maximum value (short): current positive sequence
Maximalwerte | 4 | 13119 | short (x1000) | RD | Maximum value (short): current negative sequence
Maximalwerte | 4 | 13120 | short (x10) | RD | Maximum value (short): distortion power L1 | var
Maximalwerte | 4 | 13121 | short (x10) | RD | Maximum value (short): distortion power L2 | var
Maximalwerte | 4 | 13122 | short (x10) | RD | Maximum value (short): distortion power L3 | var
Maximalwerte | 4 | 13123 | short (x10) | RD | Maximum value (short): distortion power sum | var
Maximalwerte, Zeitstempel | 6 | 3300 | uint | RD | UTC timestamp of max. value: voltage L1-N | s
Maximalwerte, Zeitstempel | 6 | 3302 | uint | RD | UTC timestamp of max. value: voltage L2-N | s
Maximalwerte, Zeitstempel | 6 | 3304 | uint | RD | UTC timestamp of max. value: voltage L3-N | s
Maximalwerte, Zeitstempel | 6 | 3306 | uint | RD | UTC timestamp of max. value: voltage L1-L2 | s
Maximalwerte, Zeitstempel | 6 | 3308 | uint | RD | UTC timestamp of max. value: voltage L2-L3 | s
Maximalwerte, Zeitstempel | 6 | 3310 | uint | RD | UTC timestamp of max. value: voltage L3-L1 | s
Maximalwerte, Zeitstempel | 6 | 3312 | uint | RD | UTC timestamp of max. value: current L1 | s
Maximalwerte, Zeitstempel | 6 | 3314 | uint | RD | UTC timestamp of max. value: current L2 | s
Maximalwerte, Zeitstempel | 6 | 3316 | uint | RD | UTC timestamp of max. value: current L3 | s
Maximalwerte, Zeitstempel | 6 | 3318 | uint | RD | UTC timestamp of max. value: current sum | s
Maximalwerte, Zeitstempel | 6 | 3320 | uint | RD | UTC timestamp of max. value: active power L1 | s
Maximalwerte, Zeitstempel | 6 | 3322 | uint | RD | UTC timestamp of max. value: active power L2 | s
Maximalwerte, Zeitstempel | 6 | 3324 | uint | RD | UTC timestamp of max. value: active power L3 | s
Maximalwerte, Zeitstempel | 6 | 3326 | uint | RD | UTC timestamp of max. value: active power sum | s
Maximalwerte, Zeitstempel | 6 | 3328 | uint | RD | UTC timestamp of max. value: reactive power L1 | s
Maximalwerte, Zeitstempel | 6 | 3330 | uint | RD | UTC timestamp of max. value: reactive power L2 | s
Maximalwerte, Zeitstempel | 6 | 3332 | uint | RD | UTC timestamp of max. value: reactive power L3 | s
Maximalwerte, Zeitstempel | 6 | 3334 | uint | RD | UTC timestamp of max. value: reactive power sum | s
Maximalwerte, Zeitstempel | 6 | 3336 | uint | RD | UTC timestamp of max. value: apparent power L1 | s
Maximalwerte, Zeitstempel | 6 | 3338 | uint | RD | UTC timestamp of max. value: apparent power L2 | s
Maximalwerte, Zeitstempel | 6 | 3340 | uint | RD | UTC timestamp of max. value: apparent power L3 | s
Maximalwerte, Zeitstempel | 6 | 3342 | uint | RD | UTC timestamp of max. value: apparent power sum | s
Maximalwerte, Zeitstempel | 6 | 3344 | uint | RD | UTC timestamp of max. value: cos(ϕ) L1 | s
Maximalwerte, Zeitstempel | 6 | 3346 | uint | RD | UTC timestamp of max. value: cos(ϕ) L2 | s
Maximalwerte, Zeitstempel | 6 | 3348 | uint | RD | UTC timestamp of max. value: cos(ϕ) L3 | s
Maximalwerte, Zeitstempel | 6 | 3350 | uint | RD | UTC timestamp of max. value: cos(ϕ) sum | s
Maximalwerte, Zeitstempel | 6 | 3352 | uint | RD | UTC timestamp of max. value: active power (fundamental oscillation) L1 | s
Maximalwerte, Zeitstempel | 6 | 3354 | uint | RD | UTC timestamp of max. value: active power (fundamental oscillation) L2 | s
Maximalwerte, Zeitstempel | 6 | 3356 | uint | RD | UTC timestamp of max. value: active power (fundamental oscillation) L3 | s
Maximalwerte, Zeitstempel | 6 | 3514 | uint | RD | UTC timestamp of max. value: THD voltage L1 | s
Maximalwerte, Zeitstempel | 6 | 3516 | uint | RD | UTC timestamp of max. value: THD voltage L2 | s
Maximalwerte, Zeitstempel | 6 | 3518 | uint | RD | UTC timestamp of max. value: THD voltage L3 | s
Maximalwerte, Zeitstempel | 6 | 3520 | uint | RD | UTC timestamp of max. value: THD current L1 | s
Maximalwerte, Zeitstempel | 6 | 3522 | uint | RD | UTC timestamp of max. value: THD current L2 | s
Maximalwerte, Zeitstempel | 6 | 3524 | uint | RD | UTC timestamp of max. value: THD current L3 | s
Maximalwerte, Zeitstempel | 6 | 3526 | uint | RD | UTC timestamp of max. value: frequency | s
Maximalwerte, Zeitstempel | 6 | 3528 | uint | RD | UTC timestamp of max. value: voltage zero sequence | s
Maximalwerte, Zeitstempel | 6 | 3530 | uint | RD | UTC timestamp of max. value: voltage positive sequence | s
Maximalwerte, Zeitstempel | 6 | 3532 | uint | RD | UTC timestamp of max. value: voltage negative sequence | s
Maximalwerte, Zeitstempel | 6 | 3534 | uint | RD | UTC timestamp of max. value: current zero sequence | s
Maximalwerte, Zeitstempel | 6 | 3536 | uint | RD | UTC timestamp of max. value: current positive sequence | s
Maximalwerte, Zeitstempel | 6 | 3538 | uint | RD | UTC timestamp of max. value: current negative sequence | s
Maximalwerte, Zeitstempel | 6 | 3540 | uint | RD | UTC timestamp of max. value: distortion power L1 | s
Maximalwerte, Zeitstempel | 6 | 3542 | uint | RD | UTC timestamp of max. value: distortion power L2 | s
Maximalwerte, Zeitstempel | 6 | 3544 | uint | RD | UTC timestamp of max. value: distortion power L3 | s
Maximalwerte, Zeitstempel | 6 | 3546 | uint | RD | UTC timestamp of max. value: distortion power sum | s
Maximalwerte, Zeitstempel | 6 | 3548 | uint | RD | UTC timestamp of max. value: mean value current L1 | s
Maximalwerte, Zeitstempel | 6 | 3550 | uint | RD | UTC timestamp of max. value: mean value current L2 | s
Maximalwerte, Zeitstempel | 6 | 3552 | uint | RD | UTC timestamp of max. value: mean value current L3 | s
Maximalwerte, Zeitstempel | 6 | 3554 | uint | RD | UTC timestamp of max. value: mean value current sum | s
Maximalwerte, Zeitstempel | 6 | 3556 | uint | RD | UTC timestamp of max. value: mean value active power L1 | s
Maximalwerte, Zeitstempel | 6 | 3558 | uint | RD | UTC timestamp of max. value: mean value active power L2 | s
Maximalwerte, Zeitstempel | 6 | 3560 | uint | RD | UTC timestamp of max. value: mean value active power L3 | s
Maximalwerte, Zeitstempel | 6 | 3562 | uint | RD | UTC timestamp of max. value: mean value active power sum | s
Maximalwerte, Zeitstempel | 6 | 3564 | uint | RD | UTC timestamp of max. value: TDD current L1 | s
Maximalwerte, Zeitstempel | 6 | 3566 | uint | RD | UTC timestamp of max. value: TDD current L2 | s
Maximalwerte, Zeitstempel | 6 | 3568 | uint | RD | UTC timestamp of max. value: TDD current L3 | s
Maximalwerte, Zeitstempel | 6 | 3570 | uint | RD | UTC timestamp of max. value: power factor L1 | s
Maximalwerte, Zeitstempel | 6 | 3572 | uint | RD | UTC timestamp of max. value: power factor L2 | s
Maximalwerte, Zeitstempel | 6 | 3574 | uint | RD | UTC timestamp of max. value: power factor L3 | s
Maximalwerte, Zeitstempel | 6 | 3576 | uint | RD | UTC timestamp of max. value: power factor sum3=Psum3/Ssum3 | s
Maximalwerte, Zeitstempel | 6 | 3578 | uint | RD | UTC timestamp of max. value: Voltage asymmetry | s
Maximalwerte, Zeitstempel | 6 | 3580 | uint | RD | UTC timestamp of max. value: Current asymmetry | s
Minimalwerte | 7 | 4000 | float | RD | Minimum value (float): voltage L1-N | V
Minimalwerte | 7 | 4002 | float | RD | Minimum value (float): voltage L2-N | V
Minimalwerte | 7 | 4004 | float | RD | Minimum value (float): voltage L3-N | V
Minimalwerte | 7 | 4006 | float | RD | Minimum value (float): voltage L1-L2 | V
Minimalwerte | 7 | 4008 | float | RD | Minimum value (float): voltage L1-L3 | V
Minimalwerte | 7 | 4010 | float | RD | Minimum value (float): voltage L3-L1 | V
Minimalwerte | 7 | 4012 | float | RD | Minimum value (float): cos(ϕ) L1
Minimalwerte | 7 | 4014 | float | RD | Minimum value (float): cos(ϕ) L2
Minimalwerte | 7 | 4016 | float | RD | Minimum value (float): cos(ϕ) L3
Minimalwerte | 7 | 4018 | float | RD | Minimum value (float): cos(ϕ) sum
Minimalwerte | 7 | 4098 | float | RD | Minimum value (float): THD voltage L1 [%] | %
Minimalwerte | 7 | 4100 | float | RD | Minimum value (float): THD voltage L2 [%] | %
Minimalwerte | 7 | 4102 | float | RD | Minimum value (float): THD voltage L3 [%] | %
Minimalwerte | 7 | 4104 | float | RD | Minimum value (float): frequency | Hz
Minimalwerte | 7 | 4106 | float | RD | Minimum value (float): voltage zero sequence
Minimalwerte | 7 | 4108 | float | RD | Minimum value (float): voltage positive sequence
Minimalwerte | 7 | 4110 | float | RD | Minimum value (float): voltage negative sequence
Minimalwerte | 7 | 4112 | float | RD | Minimum value (float): active power L1 | W
Minimalwerte | 7 | 4114 | float | RD | Minimum value (float): active power L2 | W
Minimalwerte | 7 | 4116 | float | RD | Minimum value (float): active power L3 | W
Minimalwerte | 7 | 4118 | float | RD | Minimum value (float): active power sum | W
Minimalwerte | 7 | 4120 | float | RD | Minimum value (float): power factor L1
Minimalwerte | 7 | 4122 | float | RD | Minimum value (float): power factor L2
Minimalwerte | 7 | 4124 | float | RD | Minimum value (float): power factor L3
Minimalwerte | 7 | 4126 | float | RD | Minimum value (float): power factor sum3=Psum3/Ssum3
Minimalwerte | 7 | 4128 | float | RD | Minimum value (float): THD current L1 [%] | %
Minimalwerte | 7 | 4130 | float | RD | Minimum value (float): THD current L2 [%] | %
Minimalwerte | 7 | 4132 | float | RD | Minimum value (float): THD current L3 [%] | %
Minimalwerte | 7 | 4134 | float | RD | Minimum value (float): current L1 | A
Minimalwerte | 7 | 4136 | float | RD | Minimum value (float): current L2 | A
Minimalwerte | 7 | 4138 | float | RD | Minimum value (float): current L3 | A
Minimalwerte | 7 | 4140 | float | RD | Minimum value (float): current sum | A
Minimalwerte | 7 | 4142 | float | RD | Minimum value (float): reactive power L1 | var
Minimalwerte | 7 | 4144 | float | RD | Minimum value (float): reactive power L2 | var
Minimalwerte | 7 | 4146 | float | RD | Minimum value (float): reactive power L3 | var
Minimalwerte | 7 | 4148 | float | RD | Minimum value (float): reactive power sum | var
Minimalwerte | 7 | 4150 | float | RD | Minimum value (float): apparent power L1 | VA
Minimalwerte | 7 | 4152 | float | RD | Minimum value (float): apparent power L2 | VA
Minimalwerte | 7 | 4154 | float | RD | Minimum value (float): apparent power L3 | VA
Minimalwerte | 7 | 4156 | float | RD | Minimum value (float): apparent power sum | VA
Minimalwerte | 7 | 4158 | float | RD | Minimum value (float): voltage asymmetry [%] (min) | %
Minimalwerte | 7 | 4160 | float | RD | Minimum value (float): current asymmetry [%] (min) | %
Minimalwerte | 7 | 14000 | short (x10) | RD | Minimum value (short): voltage L1-N | V
Minimalwerte | 7 | 14001 | short (x10) | RD | Minimum value (short): voltage L2-N | V
Minimalwerte | 7 | 14002 | short (x10) | RD | Minimum value (short): voltage L3-N | V
Minimalwerte | 7 | 14003 | short (x10) | RD | Minimum value (short): voltage L1-L2 | V
Minimalwerte | 7 | 14004 | short (x10) | RD | Minimum value (short): voltage L1-L3 | V
Minimalwerte | 7 | 14005 | short (x10) | RD | Minimum value (short): voltage L3-L1 | V
Minimalwerte | 7 | 14006 | short (x1000) | RD | Minimum value (short): cos(ϕ) L1
Minimalwerte | 7 | 14007 | short (x1000) | RD | Minimum value (short): cos(ϕ) L1
Minimalwerte | 7 | 14008 | short (x1000) | RD | Minimum value (short): cos(ϕ) L1
Minimalwerte | 7 | 14009 | short (x1000) | RD | Minimum value (short): cos(ϕ) L1
Minimalwerte | 7 | 14049 | short (x100) | RD | Minimum value (short): THD voltage L1 [%] | %
Minimalwerte | 7 | 14050 | short (x100) | RD | Minimum value (short): THD voltage L2 [%] | %
Minimalwerte | 7 | 14051 | short (x100) | RD | Minimum value (short): THD voltage L3 [%] | %
Minimalwerte | 7 | 14052 | short (x100) | RD | Minimum value (short): frequency | Hz
Minimalwerte | 7 | 14053 | short (x10) | RD | Minimum value (short): voltage zero sequence
Minimalwerte | 7 | 14054 | short (x10) | RD | Minimum value (short): voltage positive sequence
Minimalwerte | 7 | 14055 | short (x10) | RD | Minimum value (short): voltage negative sequence
Minimalwerte | 7 | 14056 | short (x10) | RD | Minimum value (short): active power L1 | W
Minimalwerte | 7 | 14057 | short (x10) | RD | Minimum value (short): active power L2 | W
Minimalwerte | 7 | 14058 | short (x10) | RD | Minimum value (short): active power L3 | W
Minimalwerte | 7 | 14059 | short (x10) | RD | Minimum value (short): active power sum | W
Minimalwerte, Zeitstempel | 9 | 4200 | uint | RD | UTC timestamp of min. value: voltage L1-N | s
Minimalwerte, Zeitstempel | 9 | 4202 | uint | RD | UTC timestamp of min. value: voltage L2-N | s
Minimalwerte, Zeitstempel | 9 | 4204 | uint | RD | UTC timestamp of min. value: voltage L3-N | s
Minimalwerte, Zeitstempel | 9 | 4206 | uint | RD | UTC timestamp of min. value: voltage L1-L2 | s
Minimalwerte, Zeitstempel | 9 | 4208 | uint | RD | UTC timestamp of min. value: voltage L2-L3 | s
Minimalwerte, Zeitstempel | 9 | 4210 | uint | RD | UTC timestamp of min. value: voltage L3-L1 | s
Minimalwerte, Zeitstempel | 9 | 4212 | uint | RD | UTC timestamp of min. value: cos(ϕ) L1 | s
Minimalwerte, Zeitstempel | 9 | 4214 | uint | RD | UTC timestamp of min. value: cos(ϕ) L2 | s
Minimalwerte, Zeitstempel | 9 | 4216 | uint | RD | UTC timestamp of min. value: cos(ϕ) L3 | s
Minimalwerte, Zeitstempel | 9 | 4218 | uint | RD | UTC timestamp of min. value: cos(ϕ) sum | s
Minimalwerte, Zeitstempel | 9 | 4298 | uint | RD | UTC timestamp of min. value: THD voltage L1 | s
Minimalwerte, Zeitstempel | 9 | 4300 | uint | RD | UTC timestamp of min. value: THD voltage L2 | s
Minimalwerte, Zeitstempel | 9 | 4302 | uint | RD | UTC timestamp of min. value: THD voltage L3 | s
Minimalwerte, Zeitstempel | 9 | 4304 | uint | RD | UTC timestamp of min. value: frequency | s
Minimalwerte, Zeitstempel | 9 | 4306 | uint | RD | UTC timestamp of min. value: voltage zero sequence | s
Minimalwerte, Zeitstempel | 9 | 4308 | uint | RD | UTC timestamp of min. value: voltage positive sequence | s
Minimalwerte, Zeitstempel | 9 | 4310 | uint | RD | UTC timestamp of min. value: voltage negative sequence | s
Minimalwerte, Zeitstempel | 9 | 4312 | uint | RD | UTC timestamp of min. value: active power L1 | s
Minimalwerte, Zeitstempel | 9 | 4314 | uint | RD | UTC timestamp of min. value: active power L2 | s
Minimalwerte, Zeitstempel | 9 | 4316 | uint | RD | UTC timestamp of min. value: active power L3 | s
Minimalwerte, Zeitstempel | 9 | 4318 | uint | RD | UTC timestamp of min. value: active power sum | s
Minimalwerte, Zeitstempel | 9 | 4320 | uint | RD | UTC timestamp of min. value: power factor L1 | s
Minimalwerte, Zeitstempel | 9 | 4322 | uint | RD | UTC timestamp of min. value: power factor L2 | s
Minimalwerte, Zeitstempel | 9 | 4324 | uint | RD | UTC timestamp of min. value: power factor L3 | s
Minimalwerte, Zeitstempel | 9 | 4326 | uint | RD | UTC timestamp of min. value: power factor sum | s
Minimalwerte, Zeitstempel | 9 | 4328 | uint | RD | UTC timestamp of min. value: THD current L1 | s
Minimalwerte, Zeitstempel | 9 | 4330 | uint | RD | UTC timestamp of min. value: THD current L2 | s
Minimalwerte, Zeitstempel | 9 | 4332 | uint | RD | UTC timestamp of min. value: THD current L3 | s
Minimalwerte, Zeitstempel | 9 | 4334 | uint | RD | UTC timestamp of min. value: current L1 | s
Minimalwerte, Zeitstempel | 9 | 4336 | uint | RD | UTC timestamp of min. value: current L2 | s
Minimalwerte, Zeitstempel | 9 | 4338 | uint | RD | UTC timestamp of min. value: current L3 | s
Minimalwerte, Zeitstempel | 9 | 4340 | uint | RD | UTC timestamp of min. value: current sum | s
Minimalwerte, Zeitstempel | 9 | 4342 | uint | RD | UTC timestamp of min. value: reactive power L1 | s
Minimalwerte, Zeitstempel | 9 | 4344 | uint | RD | UTC timestamp of min. value: reactive power L2 | s
Minimalwerte, Zeitstempel | 9 | 4346 | uint | RD | UTC timestamp of min. value: reactive power L3 | s
Minimalwerte, Zeitstempel | 9 | 4348 | uint | RD | UTC timestamp of min. value: reactive power sum | s
Minimalwerte, Zeitstempel | 9 | 4350 | uint | RD | UTC timestamp of min. value: apparent power L1 | s
Minimalwerte, Zeitstempel | 9 | 4352 | uint | RD | UTC timestamp of min. value: apparent power L2 | s
Minimalwerte, Zeitstempel | 9 | 4354 | uint | RD | UTC timestamp of min. value: apparent power L3 | s
Minimalwerte, Zeitstempel | 9 | 4356 | uint | RD | UTC timestamp of min. value: apparent power sum | s
Minimalwerte, Zeitstempel | 9 | 4358 | uint | RD | UTC timestamp of min. value: voltage asymmetry | s
Minimalwerte, Zeitstempel | 9 | 4360 | uint | RD | UTC timestamp of min. value: current asymmetry | s
Gleitende Mittelwerte | 12 | 57 | char | RD/WR | Time base moving mean values - Current 0=5s, 1=10s, 2=30s, 3=60s, 4=5min, 5=8min, 6=15min |  | 0 | 6
Gleitende Mittelwerte | 12 | 58 | char | RD/WR | Time base moving mean values - Power 0=5s, 1=10s, 2=30s, 3=60s, 4=5min, 5=8min, 6=15min |  | 0 | 6
Gleitende Mittelwerte | 12 | 2000 | float | RD | Mean value (float): voltage L1 | V
Gleitende Mittelwerte | 12 | 2002 | float | RD | Mean value (float): voltage L2 | V
Gleitende Mittelwerte | 12 | 2004 | float | RD | Mean value (float): voltage L3 | V
Gleitende Mittelwerte | 12 | 2006 | float | RD | Mean value (float): mean value voltage L1-L2 | V
Gleitende Mittelwerte | 12 | 2008 | float | RD | Mean value (float): mean value voltage L2-L3 | V
Gleitende Mittelwerte | 12 | 2010 | float | RD | Mean value (float): mean value voltage L3-L1 | V
Gleitende Mittelwerte | 12 | 2012 | float | RD | Mean value (float): mean value current L1 | A
Gleitende Mittelwerte | 12 | 2014 | float | RD | Mean value (float): mean value current L2 | A
Gleitende Mittelwerte | 12 | 2016 | float | RD | Mean value (float): mean value current L3 | A
Gleitende Mittelwerte | 12 | 2018 | float | RD | Mean value (float): mean value current sum | A
Gleitende Mittelwerte | 12 | 2020 | float | RD | Mean value (float): mean value active power L1 | W
Gleitende Mittelwerte | 12 | 2022 | float | RD | Mean value (float): mean value active power L2 | W
Gleitende Mittelwerte | 12 | 2024 | float | RD | Mean value (float): mean value active power L3 | W
Gleitende Mittelwerte | 12 | 2026 | float | RD | Mean value (float): mean value active power sum | W
Gleitende Mittelwerte | 12 | 2028 | float | RD | Mean value (float): mean value reactive power L1 | var
Gleitende Mittelwerte | 12 | 2030 | float | RD | Mean value (float): reactive power L2 | var
Gleitende Mittelwerte | 12 | 2032 | float | RD | Mean value (float): reactive power L3 | var
Gleitende Mittelwerte | 12 | 2034 | float | RD | Mean value (float): mean value reactive power sum | var
Gleitende Mittelwerte | 12 | 2036 | float | RD | Mean value (float): apparent power L1 | VA
Gleitende Mittelwerte | 12 | 2038 | float | RD | Mean value (float): mean value apparent power L2 | VA
Gleitende Mittelwerte | 12 | 2040 | float | RD | Mean value (float): mean value apparent power L3 | VA
Gleitende Mittelwerte | 12 | 2042 | float | RD | Mean value (float): mean value apparent power sum | VA
Gleitende Mittelwerte | 12 | 2044 | float | RD | Mean value (float): mean value cos(ϕ) L1
Gleitende Mittelwerte | 12 | 2046 | float | RD | Mean value (float): mean value cos(ϕ) L2
Gleitende Mittelwerte | 12 | 2048 | float | RD | Mean value (float): mean value cos(ϕ) L3
Gleitende Mittelwerte | 12 | 2050 | float | RD | Mean value (float): cos(ϕ) sum
Gleitende Mittelwerte | 12 | 2052 | float | RD | Mean value (float): active power, fundamental oscillation L1 | W
Gleitende Mittelwerte | 12 | 2054 | float | RD | Mean value (float): active power, fundamental oscillation L2 | W
Gleitende Mittelwerte | 12 | 2056 | float | RD | Mean value (float): active power, fundamental oscillation L3 | W
Gleitende Mittelwerte | 12 | 2214 | float | RD | Mean value (float): THD voltage L1 [%] | %
Gleitende Mittelwerte | 12 | 2216 | float | RD | Mean value (float): THD voltage L2 [%] | %
Gleitende Mittelwerte | 12 | 2218 | float | RD | Mean value (float): THD voltage L3 [%] | %
Gleitende Mittelwerte | 12 | 2220 | float | RD | Mean value (float): THD current L1 [%] | %
Gleitende Mittelwerte | 12 | 2222 | float | RD | Mean value (float): THD current L2 [%] | %
Gleitende Mittelwerte | 12 | 2224 | float | RD | Mean value (float): THD current L3 [%] | %
Gleitende Mittelwerte | 12 | 2226 | float | RD | Mean value (float): frequency | Hz
Gleitende Mittelwerte | 12 | 2228 | float | RD | Mean value (float): zero sequence voltage
Gleitende Mittelwerte | 12 | 2230 | float | RD | Mean value (float): positive sequence voltage
Gleitende Mittelwerte | 12 | 2232 | float | RD | Mean value (float): negative sequence voltage
Gleitende Mittelwerte | 12 | 2234 | float | RD | Mean value (float): zero sequence current
Gleitende Mittelwerte | 12 | 2236 | float | RD | Mean value (float): mean value positive sequence current
Gleitende Mittelwerte | 12 | 2238 | float | RD | Mean value (float): mean value negative sequence current
Gleitende Mittelwerte | 12 | 2240 | float | RD | Mean value (float): mean value distortion power L1 | var
Gleitende Mittelwerte | 12 | 2242 | float | RD | Mean value (float): mean value distortion power L2 | var
Gleitende Mittelwerte | 12 | 2244 | float | RD | Mean value (float): distortion power L3 | var
Gleitende Mittelwerte | 12 | 2246 | float | RD | Mean value (float): distortion power sum | var
Gleitende Mittelwerte | 12 | 2248 | float | RD | Mean value (float): TDD (total demand distortion) current L1 [%] | %
Gleitende Mittelwerte | 12 | 2250 | float | RD | Mean value (float): TDD (total demand distortion) current L2 [%] | %
Gleitende Mittelwerte | 12 | 2252 | float | RD | Mean value (float): TDD (total demand distortion) current L3 [%] | %
Gleitende Mittelwerte | 12 | 2254 | float | RD | Mean value (float): power factor L1
Gleitende Mittelwerte | 12 | 2256 | float | RD | Mean value (float): power factor L2
Gleitende Mittelwerte | 12 | 2258 | float | RD | Mean value (float): power factor L3
Gleitende Mittelwerte | 12 | 2260 | float | RD | Mean value (float): power factor sum3=Psum3/Ssum3
Gleitende Mittelwerte | 12 | 2294 | float | RD | Mean value (float): voltage asymmetry [%] (avg) | %
Gleitende Mittelwerte | 12 | 2296 | float | RD | Mean value (float): current asymmetry [%] (avg) | %
Gleitende Mittelwerte | 12 | 12000 | short (x10) | RD | Mean value (short): voltage L1-N | V
Gleitende Mittelwerte | 12 | 12001 | short (x10) | RD | Mean value (short): voltage L2-N | V
Gleitende Mittelwerte | 12 | 12002 | short (x10) | RD | Mean value (short): voltage L3-N | V
Gleitende Mittelwerte | 12 | 12003 | short (x10) | RD | Mean value (short): voltage L1-L2 | V
Gleitende Mittelwerte | 12 | 12004 | short (x10) | RD | Mean value (short): voltage L2-L3 | V
Gleitende Mittelwerte | 12 | 12005 | short (x10) | RD | Mean value (short): voltage L3-L1 | V
Gleitende Mittelwerte | 12 | 12006 | short (x1000) | RD | Mean value (short): current L1 | A
Gleitende Mittelwerte | 12 | 12007 | short (x1000) | RD | Mean value (short): current L2 | A
Gleitende Mittelwerte | 12 | 12008 | short (x1000) | RD | Mean value (short): current L3 | A
Gleitende Mittelwerte | 12 | 12009 | short (x1000) | RD | Mean value (short): current sum | A
Gleitende Mittelwerte | 12 | 12010 | short (x10) | RD | Mean value (short): active power L1 | W
Gleitende Mittelwerte | 12 | 12011 | short (x10) | RD | Mean value (short): active power L2 | W
Gleitende Mittelwerte | 12 | 12012 | short (x10) | RD | Mean value (short): active power L3 | W
Gleitende Mittelwerte | 12 | 12013 | short | RD | Mean value (short): active power sum | W
Gleitende Mittelwerte | 12 | 12014 | short (x10) | RD | Mean value (short): reactive power L1 | var
Gleitende Mittelwerte | 12 | 12015 | short (x10) | RD | Mean value (short): reactive power L2 | var
Gleitende Mittelwerte | 12 | 12016 | short (x10) | RD | Mean value (short): reactive power L3 | var
Gleitende Mittelwerte | 12 | 12017 | short | RD | Mean value (short): reactive power sum | var
Gleitende Mittelwerte | 12 | 12018 | short (x10) | RD | Mean value (short): apparent power L1 | VA
Gleitende Mittelwerte | 12 | 12019 | short (x10) | RD | Mean value (short): apparent power L2 | VA
Gleitende Mittelwerte | 12 | 12020 | short (x10) | RD | Mean value (short): apparent power L3 | VA
Gleitende Mittelwerte | 12 | 12021 | short | RD | Mean value (short): apparent power sum | VA
Gleitende Mittelwerte | 12 | 12022 | short (x1000) | RD | Mean value (short): cos(ϕ) L1
Gleitende Mittelwerte | 12 | 12023 | short (x1000) | RD | Mean value (short): cos(ϕ) L2
Gleitende Mittelwerte | 12 | 12024 | short (x1000) | RD | Mean value (short): cos(ϕ) L3
Gleitende Mittelwerte | 12 | 12025 | short (x1000) | RD | Mean value (short): cos(ϕ) sum
Gleitende Mittelwerte | 12 | 12026 | short (x10) | RD | Mean value (short): active power of fundamental oscillation L1 | W
Gleitende Mittelwerte | 12 | 12027 | short (x10) | RD | Mean value (short): active power of fundamental oscillation L2 | W
Gleitende Mittelwerte | 12 | 12028 | short (x10) | RD | Mean value (short): active power of fundamental oscillation L3 | W
Gleitende Mittelwerte | 12 | 12107 | short (x100) | RD | Mean value (short): THD voltage L1 | %
Gleitende Mittelwerte | 12 | 12108 | short (x100) | RD | Mean value (short): THD voltage L2 | %
Gleitende Mittelwerte | 12 | 12109 | short (x100) | RD | Mean value (short): THD voltage L3 | %
Gleitende Mittelwerte | 12 | 12110 | short (x100) | RD | Mean value (short): THD current L1 | %
Gleitende Mittelwerte | 12 | 12111 | short (x100) | RD | Mean value (short): THD current L2 | %
Gleitende Mittelwerte | 12 | 12112 | short (x100) | RD | Mean value (short): THD current L3 | %
Gleitende Mittelwerte | 12 | 12113 | short (x100) | RD | Mean value (short): frequency | Hz
Gleitende Mittelwerte | 12 | 12114 | short (x10) | RD | Mean value (short): zero sequence voltage
Gleitende Mittelwerte | 12 | 12115 | short (x10) | RD | Mean value (short): positive sequence voltage
Gleitende Mittelwerte | 12 | 12116 | short (x10) | RD | Mean value (short): negative sequence voltage
Gleitende Mittelwerte | 12 | 12117 | short (x1000) | RD | Mean value (short): zero sequence current
Gleitende Mittelwerte | 12 | 12118 | short (x1000) | RD | Mean value (short): positive sequence current
Gleitende Mittelwerte | 12 | 12119 | short (x1000) | RD | Mean value (short): negative sequence current
Gleitende Mittelwerte | 12 | 12120 | short (x10) | RD | Mean value (short): distortion power L1 | var
Gleitende Mittelwerte | 12 | 12121 | short (x10) | RD | Mean value (short): distortion power L2 | var
Gleitende Mittelwerte | 12 | 12122 | short (x10) | RD | Mean value (short): distortion power L3 | var
Gleitende Mittelwerte | 12 | 12123 | short | RD | Mean value (short): distortion power sum | var
Maximalwerte der gleitenden Mittelwerte | 14 | 3248 | float | RD | Maximum values of mean values (float): current L1 | A
Maximalwerte der gleitenden Mittelwerte | 14 | 3250 | float | RD | Maximum values of mean values (float): current L2 | A
Maximalwerte der gleitenden Mittelwerte | 14 | 3252 | float | RD | Maximum values of mean values (float): current L3 | A
Maximalwerte der gleitenden Mittelwerte | 14 | 3254 | float | RD | Maximum values of mean values (float): current sum | A
Maximalwerte der gleitenden Mittelwerte | 14 | 3256 | float | RD | Maximum values of mean values (float): active power L1 | W
Maximalwerte der gleitenden Mittelwerte | 14 | 3258 | float | RD | Maximum values of mean values (float): active power L2 | W
Maximalwerte der gleitenden Mittelwerte | 14 | 3260 | float | RD | Maximum values of mean values (float): active power L3 | W
Maximalwerte der gleitenden Mittelwerte | 14 | 3262 | float | RD | Maximum values of mean values (float): active power sum | W
Maximalwerte der gleitenden Mittelwerte | 14 | 13124 | short (x1000) | RD | Maximum values of mean values (short): current L1 | A
Maximalwerte der gleitenden Mittelwerte | 14 | 13125 | short (x1000) | RD | Maximum values of mean values (short): current L2 | A
Maximalwerte der gleitenden Mittelwerte | 14 | 13126 | short (x1000) | RD | Maximum values of mean values (short): current L3 | A
Maximalwerte der gleitenden Mittelwerte | 14 | 13128 | short (x10) | RD | Maximum values of mean values (short): active power L1 | A
Maximalwerte der gleitenden Mittelwerte | 14 | 13129 | short (x10) | RD | Maximum values of mean values (short): active power L2 | A
Maximalwerte der gleitenden Mittelwerte | 14 | 13130 | short (x10) | RD | Maximum values of mean values (short): active power L3 | A
Gerasterte Mittelwerte | 16 | 31504 | ushort | RD/WR | averaging interval for Gridded Mean Values in Seconds | s | 60 | 3600
Gerasterte Mittelwerte | 16 | 32000 | float | RD | Gridded mean values (float): maximum voltage L1 | V
Gerasterte Mittelwerte | 16 | 32002 | float | RD | Gridded mean values (float): maximum voltage L2 | V
Gerasterte Mittelwerte | 16 | 32004 | float | RD | Gridded mean values (float): maximum voltage L3 | V
Gerasterte Mittelwerte | 16 | 32008 | float | RD | Gridded mean values (float): maximum voltage L1-L2 | V
Gerasterte Mittelwerte | 16 | 32010 | float | RD | Gridded mean values (float): maximum voltage L2-L3 | V
Gerasterte Mittelwerte | 16 | 32012 | float | RD | Gridded mean values (float): maximum voltage L3-L1 | V
Gerasterte Mittelwerte | 16 | 32016 | float | RD | Gridded mean values (float): maximum current L1 | A
Gerasterte Mittelwerte | 16 | 32018 | float | RD | Gridded mean values (float): maximum current L2 | A
Gerasterte Mittelwerte | 16 | 32020 | float | RD | Gridded mean values (float): maximum current L3 | A
Gerasterte Mittelwerte | 16 | 32022 | float | RD | Gridded mean values (float): maximum current L4 | A
Gerasterte Mittelwerte | 16 | 32024 | float | RD | Gridded mean values (float): sum maximum current L1-L3 | A
Gerasterte Mittelwerte | 16 | 32026 | float | RD | Gridded mean values (float): sum maximum current L1-L4 | A
Gerasterte Mittelwerte | 16 | 32028 | float | RD | Gridded mean values (float): maximum active power L1 | W
Gerasterte Mittelwerte | 16 | 32030 | float | RD | Gridded mean values (float): maximum active power L2 | W
Gerasterte Mittelwerte | 16 | 32032 | float | RD | Gridded mean values (float): maximum active power L3 | W
Gerasterte Mittelwerte | 16 | 32036 | float | RD | Gridded mean values (float): maximum total active power | W
Gerasterte Mittelwerte | 16 | 32040 | float | RD | Gridded mean values (float): maximum reactive power L1 | VA
Gerasterte Mittelwerte | 16 | 32042 | float | RD | Gridded mean values (float): maximum reactive power L2 | VA
Gerasterte Mittelwerte | 16 | 32044 | float | RD | Gridded mean values (float): maximum reactive power L3 | VA
Gerasterte Mittelwerte | 16 | 32048 | float | RD | Gridded mean values (float): maximum total reactive power | VA
Gerasterte Mittelwerte | 16 | 32052 | float | RD | Gridded mean values (float): maximum apparent power L1 | var
Gerasterte Mittelwerte | 16 | 32054 | float | RD | Gridded mean values (float): maximum apparent power L2 | var
Gerasterte Mittelwerte | 16 | 32056 | float | RD | Gridded mean values (float): maximum apparent power L3 | var
Gerasterte Mittelwerte | 16 | 32060 | float | RD | Gridded mean values (float): maximum total apparent power | var
Gerasterte Mittelwerte | 16 | 32064 | float | RD | Gridded mean values (float): maximum cos(phi) L1
Gerasterte Mittelwerte | 16 | 32066 | float | RD | Gridded mean values (float): maximum cos(phi) L2
Gerasterte Mittelwerte | 16 | 32068 | float | RD | Gridded mean values (float): maximum cos(phi) L3
Gerasterte Mittelwerte | 16 | 32072 | float | RD | Gridded mean values (float): maximum cos(phi)
Gerasterte Mittelwerte | 16 | 32076 | float | RD | Gridded mean values (float): minimum voltage L1 | V
Gerasterte Mittelwerte | 16 | 32078 | float | RD | Gridded mean values (float): minimum voltage L2 | V
Gerasterte Mittelwerte | 16 | 32080 | float | RD | Gridded mean values (float): minimum voltage L3 | V
Gerasterte Mittelwerte | 16 | 32084 | float | RD | Gridded mean values (float): minimum voltage L1-L2 | V
Gerasterte Mittelwerte | 16 | 32086 | float | RD | Gridded mean values (float): minimum voltage L2-L3 | V
Gerasterte Mittelwerte | 16 | 32088 | float | RD | Gridded mean values (float): minimum voltage L3-L1 | V
Gerasterte Mittelwerte | 16 | 32092 | float | RD | Gridded mean values (float): minimum current L1 | A
Gerasterte Mittelwerte | 16 | 32094 | float | RD | Gridded mean values (float): minimum current L2 | A
Gerasterte Mittelwerte | 16 | 32096 | float | RD | Gridded mean values (float): minimum current L3 | A
Gerasterte Mittelwerte | 16 | 32098 | float | RD | Gridded mean values (float): minimum current L4 | A
Gerasterte Mittelwerte | 16 | 32100 | float | RD | Gridded mean values (float): sum minimum current L1-L3 | A
Gerasterte Mittelwerte | 16 | 32102 | float | RD | Gridded mean values (float): sum minimum current L1-L4 | A
Gerasterte Mittelwerte | 16 | 32104 | float | RD | Gridded mean values (float): minimum active power L1 | W
Gerasterte Mittelwerte | 16 | 32106 | float | RD | Gridded mean values (float): minimum active power L2 | W
Gerasterte Mittelwerte | 16 | 32108 | float | RD | Gridded mean values (float): minimum active power L3 | W
Gerasterte Mittelwerte | 16 | 32112 | float | RD | Gridded mean values (float): minimum total active power | W
Gerasterte Mittelwerte | 16 | 32116 | float | RD | Gridded mean values (float): minimum reactive power L1 | VA
Gerasterte Mittelwerte | 16 | 32118 | float | RD | Gridded mean values (float): minimum reactive power L2 | VA
Gerasterte Mittelwerte | 16 | 32120 | float | RD | Gridded mean values (float): minimum reactive power L3 | VA
Gerasterte Mittelwerte | 16 | 32124 | float | RD | Gridded mean values (float): minimum total reactive power | VA
Gerasterte Mittelwerte | 16 | 32128 | float | RD | Gridded mean values (float): minimum apparent power L1 | var
Gerasterte Mittelwerte | 16 | 32130 | float | RD | Gridded mean values (float): minimum apparent power L2 | var
Gerasterte Mittelwerte | 16 | 32132 | float | RD | Gridded mean values (float): minimum apparent power L3 | var
Gerasterte Mittelwerte | 16 | 32136 | float | RD | Gridded mean values (float): minimum total apparent power | var
Gerasterte Mittelwerte | 16 | 32140 | float | RD | Gridded mean values (float): minimum cos(phi) L1
Gerasterte Mittelwerte | 16 | 32142 | float | RD | Gridded mean values (float): minimum cos(phi) L2
Gerasterte Mittelwerte | 16 | 32144 | float | RD | Gridded mean values (float): minimum cos(phi) L3
Gerasterte Mittelwerte | 16 | 32148 | float | RD | Gridded mean values (float): minimum cos(phi)
Gerasterte Mittelwerte | 16 | 32152 | float | RD | Gridded mean values (float): average voltage L1 | V
Gerasterte Mittelwerte | 16 | 32154 | float | RD | Gridded mean values (float): average voltage L2 | V
Gerasterte Mittelwerte | 16 | 32156 | float | RD | Gridded mean values (float): average voltage L3 | V
Gerasterte Mittelwerte | 16 | 32160 | float | RD | Gridded mean values (float): average voltage L1-L2 | V
Gerasterte Mittelwerte | 16 | 32162 | float | RD | Gridded mean values (float): average voltage L2-L3 | V
Gerasterte Mittelwerte | 16 | 32164 | float | RD | Gridded mean values (float): average voltage L3-L1 | V
Gerasterte Mittelwerte | 16 | 32168 | float | RD | Gridded mean values (float): average current L1 | A
Gerasterte Mittelwerte | 16 | 32170 | float | RD | Gridded mean values (float): average current L2 | A
Gerasterte Mittelwerte | 16 | 32172 | float | RD | Gridded mean values (float): average current L3 | A
Gerasterte Mittelwerte | 16 | 32174 | float | RD | Gridded mean values (float): average current L4 | A
Gerasterte Mittelwerte | 16 | 32176 | float | RD | Gridded mean values (float): sum average current L1-L3 | A
Gerasterte Mittelwerte | 16 | 32178 | float | RD | Gridded mean values (float): sum average current L1-L4 | A
Gerasterte Mittelwerte | 16 | 32180 | float | RD | Gridded mean values (float): average active power L1 | W
Gerasterte Mittelwerte | 16 | 32182 | float | RD | Gridded mean values (float): average active power L2 | W
Gerasterte Mittelwerte | 16 | 32184 | float | RD | Gridded mean values (float): average active power L3 | W
Gerasterte Mittelwerte | 16 | 32188 | float | RD | Gridded mean values (float): average total active power | W
Gerasterte Mittelwerte | 16 | 32192 | float | RD | Gridded mean values (float): average apparent power L1 | VA
Gerasterte Mittelwerte | 16 | 32194 | float | RD | Gridded mean values (float): average apparent power L2 | VA
Gerasterte Mittelwerte | 16 | 32196 | float | RD | Gridded mean values (float): average apparent power L3 | VA
Gerasterte Mittelwerte | 16 | 32200 | float | RD | Gridded mean values (float): average total apparent power | VA
Gerasterte Mittelwerte | 16 | 32204 | float | RD | Gridded mean values (float): average reactive power L1 | var
Gerasterte Mittelwerte | 16 | 32206 | float | RD | Gridded mean values (float): average reactive power L2 | var
Gerasterte Mittelwerte | 16 | 32208 | float | RD | Gridded mean values (float): average reactive power L3 | var
Gerasterte Mittelwerte | 16 | 32212 | float | RD | Gridded mean values (float): average total reactive power | var
Gerasterte Mittelwerte | 16 | 32216 | float | RD | Gridded mean values (float): average cos(phi) L1
Gerasterte Mittelwerte | 16 | 32218 | float | RD | Gridded mean values (float): average cos(phi) L2
Gerasterte Mittelwerte | 16 | 32220 | float | RD | Gridded mean values (float): average cos(phi) L3
Gerasterte Mittelwerte | 16 | 32224 | float | RD | Gridded mean values (float): average cos(phi)
Gerasterte Mittelwerte | 16 | 32609 | uint | RD | Gridded mean values (float): UTC timestamp
Schleppzeigerwerte | 17 | 7000 | float | RD | Drag indicator: highest value current L1 | A
Schleppzeigerwerte | 17 | 7002 | float | RD | Drag indicator: highest value current L2 | A
Schleppzeigerwerte | 17 | 7004 | float | RD | Drag indicator: highest value current L3 | A
Schleppzeigerwerte | 17 | 7006 | uint | RD | Drag indicator: point in time [UTC], highest value current L1 | s
Schleppzeigerwerte | 17 | 7008 | uint | RD | Drag indicator: point in time [UTC], highest value current L2 | s
Schleppzeigerwerte | 17 | 7010 | uint | RD | Drag indicator: point in time [UTC], highest value current L3 | s
Schleppzeigerwerte | 17 | 7012 | float | RD | Drag indicator: highest value apparent power L1 | VA
Schleppzeigerwerte | 17 | 7014 | float | RD | Drag indicator: highest value apparent power L2 | VA
Schleppzeigerwerte | 17 | 7016 | float | RD | Drag indicator: highest value apparent power L3 | VA
Schleppzeigerwerte | 17 | 7018 | float | RD | Drag indicator: highest value apparent power sum | VA
Schleppzeigerwerte | 17 | 7020 | uint | RD | Drag indicator: point in time [UTC], highest value apparent power L1 | s
Schleppzeigerwerte | 17 | 7022 | uint | RD | Drag indicator: point in time [UTC], highest value apparent power L2 | s
Schleppzeigerwerte | 17 | 7024 | uint | RD | Drag indicator: point in time [UTC], highest value apparent power L3 | s
Schleppzeigerwerte | 17 | 7026 | uint | RD | Drag indicator: point in time [UTC], highest value apparent power sum | s
Schleppzeigerwerte | 17 | 7028 | float | RD | Drag indicator: highest value active power L1, consumed | W
Schleppzeigerwerte | 17 | 7030 | float | RD | Drag indicator: highest value active power L2, consumed | W
Schleppzeigerwerte | 17 | 7032 | float | RD | Drag indicator: highest value active power L3, consumed | W
Schleppzeigerwerte | 17 | 7034 | float | RD | Drag indicator: highest value active power sum, consumed | W
Schleppzeigerwerte | 17 | 7036 | uint | RD | Drag indicator: point in time [UTC], highest value active power L1, consumed | s
Schleppzeigerwerte | 17 | 7038 | uint | RD | Drag indicator: point in time [UTC], highest value active power L2, consumed | s
Schleppzeigerwerte | 17 | 7040 | uint | RD | Drag indicator: point in time [UTC], highest value active power L3, consumed | s
Schleppzeigerwerte | 17 | 7042 | uint | RD | Drag indicator: point in time [UTC], highest value active power sum, consumed | s
Schleppzeigerwerte | 17 | 7044 | float | RD | Drag indicator: highest value active power L1, delivered | W
Schleppzeigerwerte | 17 | 7046 | float | RD | Drag indicator: highest value active power L2, delivered | W
Schleppzeigerwerte | 17 | 7048 | float | RD | Drag indicator: highest value active power L3, delivered | W
Schleppzeigerwerte | 17 | 7050 | float | RD | Drag indicator: highest value active power sum, delivered | W
Schleppzeigerwerte | 17 | 7052 | uint | RD | Drag indicator: point in time [UTC], highest value active power L1, delivered | s
Schleppzeigerwerte | 17 | 7054 | uint | RD | Drag indicator: point in time [UTC], highest value active power L2, delivered | s
Schleppzeigerwerte | 17 | 7056 | uint | RD | Drag indicator: point in time [UTC], highest value active power L3, delivered | s
Schleppzeigerwerte | 17 | 7058 | uint | RD | Drag indicator: point in time [UTC], highest value active power sum, delivered | s
Schleppzeigerwerte | 17 | 7060 | float | RD | Drag indicator: 2. highest value current L1 | A
Schleppzeigerwerte | 17 | 7062 | float | RD | Drag indicator: 2. highest value current L2 | A
Schleppzeigerwerte | 17 | 7064 | float | RD | Drag indicator: 2. highest value current L3 | A
Schleppzeigerwerte | 17 | 7066 | uint | RD | Drag indicator: point in time [UTC], 2. highest value current L1 | s
Schleppzeigerwerte | 17 | 7068 | uint | RD | Drag indicator: point in time [UTC], 2. highest value current L2 | s
Schleppzeigerwerte | 17 | 7070 | uint | RD | Drag indicator: point in time [UTC], 2. highest value current L3 | s
Schleppzeigerwerte | 17 | 7072 | float | RD | Drag indicator: 2. highest value apparent power L1 | VA
Schleppzeigerwerte | 17 | 7074 | float | RD | Drag indicator: 2. highest value apparent power L2 | VA
Schleppzeigerwerte | 17 | 7076 | float | RD | Drag indicator: 2. highest value apparent power L3 | VA
Schleppzeigerwerte | 17 | 7078 | float | RD | Drag indicator: 2. highest value apparent power sum | VA
Schleppzeigerwerte | 17 | 7080 | uint | RD | Drag indicator: point in time [UTC], 2. highest value apparent power L1 | s
Schleppzeigerwerte | 17 | 7082 | uint | RD | Drag indicator: point in time [UTC], 2. highest value apparent power L2 | s
Schleppzeigerwerte | 17 | 7084 | uint | RD | Drag indicator: point in time [UTC], 2. highest value apparent power L3 | s
Schleppzeigerwerte | 17 | 7086 | uint | RD | Drag indicator: point in time [UTC], 2. highest value apparent power sum | s
Schleppzeigerwerte | 17 | 7088 | float | RD | Drag indicator: 2. highest value active power L1, consumed | W
Schleppzeigerwerte | 17 | 7090 | float | RD | Drag indicator: 2. highest value active power L2, consumed | W
Schleppzeigerwerte | 17 | 7092 | float | RD | Drag indicator: 2. highest value active power L3, consumed | W
Schleppzeigerwerte | 17 | 7094 | float | RD | Drag indicator: 2. highest value active power sum, consumed | W
Schleppzeigerwerte | 17 | 7096 | uint | RD | Drag indicator: point in time [UTC], 2. highest value active power L1, consumed | s
Schleppzeigerwerte | 17 | 7098 | uint | RD | Drag indicator: point in time [UTC], 2. highest value active power L2, consumed | s
Schleppzeigerwerte | 17 | 7100 | uint | RD | Drag indicator: point in time [UTC], 2. highest value active power L3, consumed | s
Schleppzeigerwerte | 17 | 7102 | uint | RD | Drag indicator: point in time [UTC], 2. highest value active power sum, consumed | s
Schleppzeigerwerte | 17 | 7104 | float | RD | Drag indicator: 2. highest value active power L1, delivered | W
Schleppzeigerwerte | 17 | 7106 | float | RD | Drag indicator: 2. highest value active power L2, delivered | W
Schleppzeigerwerte | 17 | 7108 | float | RD | Drag indicator: 2. highest value active power L3, delivered | W
Schleppzeigerwerte | 17 | 7110 | float | RD | Drag indicator: 2. highest value active power sum, delivered | W
Schleppzeigerwerte | 17 | 7112 | uint | RD | Drag indicator: point in time [UTC], 2. highest value active power L1, delivered | s
Schleppzeigerwerte | 17 | 7114 | uint | RD | Drag indicator: point in time [UTC], 2. highest value active power L2, delivered | s
Schleppzeigerwerte | 17 | 7116 | uint | RD | Drag indicator: point in time [UTC], 2. highest value active power L3, delivered | s
Schleppzeigerwerte | 17 | 7118 | uint | RD | Drag indicator: point in time [UTC], 2. highest value active power sum, delivered | s
Schleppzeigerwerte | 17 | 7120 | float | RD | Drag indicator: 3. highest value current L1 | A
Schleppzeigerwerte | 17 | 7122 | float | RD | Drag indicator: 3. highest value current L2 | A
Schleppzeigerwerte | 17 | 7124 | float | RD | Drag indicator: 3. highest value current L3 | A
Schleppzeigerwerte | 17 | 7126 | uint | RD | Drag indicator: point in time [UTC], 3. highest value current L1 | s
Schleppzeigerwerte | 17 | 7128 | uint | RD | Drag indicator: point in time [UTC], 3. highest value current L2 | s
Schleppzeigerwerte | 17 | 7130 | uint | RD | Drag indicator: point in time [UTC], 3. highest value current L3 | s
Schleppzeigerwerte | 17 | 7132 | float | RD | Drag indicator: 3. highest value apparent power L1 | VA
Schleppzeigerwerte | 17 | 7134 | float | RD | Drag indicator: 3. highest value apparent power L2 | VA
Schleppzeigerwerte | 17 | 7136 | float | RD | Drag indicator: 3. highest value apparent power L3 | VA
Schleppzeigerwerte | 17 | 7138 | float | RD | Drag indicator: 3. highest value apparent power sum | VA
Schleppzeigerwerte | 17 | 7140 | uint | RD | Drag indicator: point in time [UTC], 3. highest value apparent power L1 | s
Schleppzeigerwerte | 17 | 7142 | uint | RD | Drag indicator: point in time [UTC], 3. highest value apparent power L2 | s
Schleppzeigerwerte | 17 | 7144 | uint | RD | Drag indicator: point in time [UTC], 3. highest value apparent power L3 | s
Schleppzeigerwerte | 17 | 7146 | uint | RD | Drag indicator: point in time [UTC], 3. highest value apparent power sum | s
Schleppzeigerwerte | 17 | 7148 | float | RD | Drag indicator: 3. highest value active power L1, consumed | W
Schleppzeigerwerte | 17 | 7150 | float | RD | Drag indicator: 3. highest value active power L2, consumed | W
Schleppzeigerwerte | 17 | 7152 | float | RD | Drag indicator: 3. highest value active power L3, consumed | W
Schleppzeigerwerte | 17 | 7154 | float | RD | Drag indicator: 3. highest value active power sum, consumed | W
Schleppzeigerwerte | 17 | 7156 | uint | RD | Drag indicator: point in time [UTC], 3. highest value active power L1, consumed | s
Schleppzeigerwerte | 17 | 7158 | uint | RD | Drag indicator: point in time [UTC], 3. highest value active power L2, consumed | s
Schleppzeigerwerte | 17 | 7160 | uint | RD | Drag indicator: point in time [UTC], 3. highest value active power L3, consumed | s
Schleppzeigerwerte | 17 | 7162 | uint | RD | Drag indicator: point in time [UTC], 3. highest value active power sum, consumed | s
Schleppzeigerwerte | 17 | 7164 | float | RD | Drag indicator: 3. highest value active power L1, delivered | W
Schleppzeigerwerte | 17 | 7166 | float | RD | Drag indicator: 3. highest value active power L2, delivered | W
Schleppzeigerwerte | 17 | 7168 | float | RD | Drag indicator: 3. highest value active power L3, delivered | W
Schleppzeigerwerte | 17 | 7170 | float | RD | Drag indicator: 3. highest value active power sum, delivered | W
Schleppzeigerwerte | 17 | 7172 | uint | RD | Drag indicator: point in time [UTC], 3. highest value active power L1, delivered | s
Schleppzeigerwerte | 17 | 7174 | uint | RD | Drag indicator: point in time [UTC], 3. highest value active power L2, delivered | s
Schleppzeigerwerte | 17 | 7176 | uint | RD | Drag indicator: point in time [UTC], 3. highest value active power L3, delivered | s
Schleppzeigerwerte | 17 | 7178 | uint | RD | Drag indicator: point in time [UTC], 3. highest value active power sum, delivered | s
Energiewerte | 20 | 5000 | float | RD | Active Energy L1, consumed | Wh
Energiewerte | 20 | 5002 | float | RD | Active Energy L2, consumed | Wh
Energiewerte | 20 | 5004 | float | RD | Active Energy L3, consumed | Wh
Energiewerte | 20 | 5006 | float | RD | Active Energy sum, consumed | Wh
Energiewerte | 20 | 5008 | float | RD | Active Energy L1, consumed, HT | Wh
Energiewerte | 20 | 5010 | float | RD | Active Energy L2, consumed, HT | Wh
Energiewerte | 20 | 5012 | float | RD | Active Energy L3, consumed, HT | Wh
Energiewerte | 20 | 5014 | float | RD | Active Energy sum, consumed, HT | Wh
Energiewerte | 20 | 5016 | float | RD | Active Energy L1, consumed, NT | Wh
Energiewerte | 20 | 5018 | float | RD | Active Energy L2, consumed, NT | Wh
Energiewerte | 20 | 5020 | float | RD | Active Energy L3, consumed, NT | Wh
Energiewerte | 20 | 5022 | float | RD | Active Energy sum, consumed, NT | Wh
Energiewerte | 20 | 5024 | float | RD | Apparent Energy L1 | VAh
Energiewerte | 20 | 5026 | float | RD | Apparent Energy L2 | VAh
Energiewerte | 20 | 5028 | float | RD | Apparent Energy L3 | VAh
Energiewerte | 20 | 5030 | float | RD | Apparent Energy, total | VAh
Energiewerte | 20 | 5032 | float | RD | Apparent Energy L1, HT | VAh
Energiewerte | 20 | 5034 | float | RD | Apparent Energy L1, HT | VAh
Energiewerte | 20 | 5036 | float | RD | Apparent Energy L3, HT | VAh
Energiewerte | 20 | 5038 | float | RD | Apparent Energy, total, HT | VAh
Energiewerte | 20 | 5040 | float | RD | Apparent Energy L1, NT | VAh
Energiewerte | 20 | 5042 | float | RD | Apparent Energy L2, NT | VAh
Energiewerte | 20 | 5044 | float | RD | Apparent Energy L3, NT | VAh
Energiewerte | 20 | 5046 | float | RD | Apparent Energy, total, NT | VAh
Energiewerte | 20 | 5048 | float | RD | Reactive Energy L1, inductive | varh
Energiewerte | 20 | 5050 | float | RD | Reactive Energy L2, inductive | varh
Energiewerte | 20 | 5052 | float | RD | Reactive Energy L3, inductive | varh
Energiewerte | 20 | 5054 | float | RD | Reactive Energy sum, inductive | varh
Energiewerte | 20 | 5056 | float | RD | Reactive Energy L1, inductive, HT | varh
Energiewerte | 20 | 5058 | float | RD | Reactive Energy L2, inductive, HT | varh
Energiewerte | 20 | 5060 | float | RD | Reactive Energy L3, inductive, HT | varh
Energiewerte | 20 | 5062 | float | RD | Reactive Energy, total, inductive, HT | varh
Energiewerte | 20 | 5064 | float | RD | Reactive Energy L1, inductive, NT | varh
Energiewerte | 20 | 5066 | float | RD | Reactive Energy L2, inductive, NT | varh
Energiewerte | 20 | 5068 | float | RD | Reactive Energy L3, inductive, NT | varh
Energiewerte | 20 | 5070 | float | RD | Reactive Energy, total, inductive, NT | varh
Energiewerte | 20 | 5072 | float | RD | Active Energy L1, delivered | Wh
Energiewerte | 20 | 5074 | float | RD | Active Energy L2, delivered | Wh
Energiewerte | 20 | 5076 | float | RD | Active Energy L3, delivered | Wh
Energiewerte | 20 | 5078 | float | RD | Active Energy sum, delivered | Wh
Energiewerte | 20 | 5080 | float | RD | Reactive Energy L1, capazitive | varh
Energiewerte | 20 | 5082 | float | RD | Reactive Energy L2, capazitive | varh
Energiewerte | 20 | 5084 | float | RD | Reactive Energy L3, capazitive | varh
Energiewerte | 20 | 5086 | float | RD | Reactive Energy sum, capazitive | varh
Energiewerte | 20 | 5088 | float | RD | Active Energy sum, without return travel block | Wh
Energiewerte | 20 | 5090 | float | RD | Reactive Energy sum, without return travel block | varh
Energiewerte | 20 | 5092 | float | RD | Reactive Energy L1, inductive, consumed | varh
Energiewerte | 20 | 5094 | float | RD | Reactive Energy L2, inductive, consumed | varh
Energiewerte | 20 | 5096 | float | RD | Reactive Energy L3, inductive, consumed | varh
Energiewerte | 20 | 5098 | float | RD | Reactive Energy sum, inductive, consumed | varh
Energiewerte | 20 | 5100 | float | RD | Reactive Energy L1, capazitive, consumed | varh
Energiewerte | 20 | 5102 | float | RD | Reactive Energy L2, capazitive, consumed | varh
Energiewerte | 20 | 5104 | float | RD | Reactive Energy L3, capazitive, consumed | varh
Energiewerte | 20 | 5106 | float | RD | Reactive Energy sum, capazitive, consumed | varh
Energiewerte | 20 | 5108 | float | RD | Reactive Energy L1, inductive, delivered | varh
Energiewerte | 20 | 5110 | float | RD | Reactive Energy L2, inductive, delivered | varh
Energiewerte | 20 | 5112 | float | RD | Reactive Energy L3, inductive, delivered | varh
Energiewerte | 20 | 5114 | float | RD | Reactive Energy sum, inductive, delivered | varh
Energiewerte | 20 | 5116 | float | RD | Reactive Energy L1, capazitive, delivered | varh
Energiewerte | 20 | 5118 | float | RD | Reactive Energy L2, capazitive, delivered | varh
Energiewerte | 20 | 5120 | float | RD | Reactive Energy L3, capazitive, delivered | varh
Energiewerte | 20 | 5122 | float | RD | Reactive Energy sum, capazitive, delivered | varh
Energiewerte | 20 | 5124 | float | RD | Active Energy (consumed), max. monthly value, jan., even year | Wh
Energiewerte | 20 | 5126 | float | RD | Active Energy (consumed), max. monthly value, feb., even year | Wh
Energiewerte | 20 | 5128 | float | RD | Active Energy (consumed), max. monthly value, mar., even year | Wh
Energiewerte | 20 | 5130 | float | RD | Active Energy (consumed), max. monthly value, apr., even year | Wh
Energiewerte | 20 | 5132 | float | RD | Active Energy (consumed), max. monthly value, may., even year | Wh
Energiewerte | 20 | 5134 | float | RD | Active Energy (consumed), max. monthly value, jun., even year | Wh
Energiewerte | 20 | 5136 | float | RD | Active Energy (consumed), max. monthly value, jul., even year | Wh
Energiewerte | 20 | 5138 | float | RD | Active Energy (consumed), max. monthly value, aug., even year | Wh
Energiewerte | 20 | 5140 | float | RD | Active Energy (consumed), max. monthly value, sep., even year | Wh
Energiewerte | 20 | 5142 | float | RD | Active Energy (consumed), max. monthly value, oct., even year | Wh
Energiewerte | 20 | 5144 | float | RD | Active Energy (consumed), max. monthly value, nov., even year | Wh
Energiewerte | 20 | 5146 | float | RD | Active Energy (consumed), max. monthly value, dec., even year | Wh
Energiewerte | 20 | 5148 | float | RD | Active Energy (consumed), max. monthly value, jan., uneven year | Wh
Energiewerte | 20 | 5150 | float | RD | Active Energy (consumed), max. monthly value, feb., uneven year | Wh
Energiewerte | 20 | 5152 | float | RD | Active Energy (consumed), max. monthly value, mar., uneven year | Wh
Energiewerte | 20 | 5154 | float | RD | Active Energy (consumed), max. monthly value, apr., uneven year | Wh
Energiewerte | 20 | 5156 | float | RD | Active Energy (consumed), max. monthly value, may., uneven year | Wh
Energiewerte | 20 | 5158 | float | RD | Active Energy (consumed), max. monthly value, jun., uneven year | Wh
Energiewerte | 20 | 5160 | float | RD | Active Energy (consumed), max. monthly value, jul., uneven year | Wh
Energiewerte | 20 | 5162 | float | RD | Active Energy (consumed), max. monthly value, aug., uneven year | Wh
Energiewerte | 20 | 5164 | float | RD | Active Energy (consumed), max. monthly value, sep., uneven year | Wh
Energiewerte | 20 | 5166 | float | RD | Active Energy (consumed), max. monthly value, oct., uneven year | Wh
Energiewerte | 20 | 5168 | float | RD | Active Energy (consumed), max. monthly value, nov., uneven year | Wh
Energiewerte | 20 | 5170 | float | RD | Active Energy (consumed), max. monthly value, dec., uneven year | Wh
Energiewerte | 20 | 5172 | float | RD | Apparent Energy, max. monthly value, jan., even year | VAh
Energiewerte | 20 | 5174 | float | RD | Apparent Energy, max. monthly value, feb., even year | VAh
Energiewerte | 20 | 5176 | float | RD | Apparent Energy, max. monthly value, mar., even year | VAh
Energiewerte | 20 | 5178 | float | RD | Apparent Energy, max. monthly value, apr., even year | VAh
Energiewerte | 20 | 5180 | float | RD | Apparent Energy, max. monthly value, may., even year | VAh
Energiewerte | 20 | 5182 | float | RD | Apparent Energy, max. monthly value, jun., even year | VAh
Energiewerte | 20 | 5184 | float | RD | Apparent Energy, max. monthly value, jul., even year | VAh
Energiewerte | 20 | 5186 | float | RD | Apparent Energy, max. monthly value, aug., even year | VAh
Energiewerte | 20 | 5188 | float | RD | Apparent Energy, max. monthly value, sep., even year | VAh
Energiewerte | 20 | 5190 | float | RD | Apparent Energy, max. monthly value, oct., even year | VAh
Energiewerte | 20 | 5192 | float | RD | Apparent Energy, max. monthly value, nov., even year | VAh
Energiewerte | 20 | 5194 | float | RD | Apparent Energy, max. monthly value, dec., even year | VAh
Energiewerte | 20 | 5196 | float | RD | Apparent Energy, max. monthly value, jan., uneven year | VAh
Energiewerte | 20 | 5198 | float | RD | Apparent Energy, max. monthly value, feb., uneven year | VAh
Energiewerte | 20 | 5200 | float | RD | Apparent Energy, max. monthly value, mar., uneven year | VAh
Energiewerte | 20 | 5202 | float | RD | Apparent Energy, max. monthly value, apr., uneven year | VAh
Energiewerte | 20 | 5204 | float | RD | Apparent Energy, max. monthly value, may., uneven year | VAh
Energiewerte | 20 | 5206 | float | RD | Apparent Energy, max. monthly value, jun., uneven year | VAh
Energiewerte | 20 | 5208 | float | RD | Apparent Energy, max. monthly value, jul., uneven year | VAh
Energiewerte | 20 | 5210 | float | RD | Apparent Energy, max. monthly value, aug., uneven year | VAh
Energiewerte | 20 | 5212 | float | RD | Apparent Energy, max. monthly value, sep., uneven year | VAh
Energiewerte | 20 | 5214 | float | RD | Apparent Energy, max. monthly value, oct., uneven year | VAh
Energiewerte | 20 | 5216 | float | RD | Apparent Energy, max. monthly value, nov., uneven year | VAh
Energiewerte | 20 | 5218 | float | RD | Apparent Energy, max. monthly value, dec., uneven year | VAh
Energiewerte | 20 | 5220 | float | RD | Reactive Energy (ind.), max. monthly value, jan., even year | varh
Energiewerte | 20 | 5222 | float | RD | Reactive Energy (ind.), max. monthly value, feb., even year | varh
Energiewerte | 20 | 5224 | float | RD | Reactive Energy (ind.), max. monthly value, mar., even year | varh
Energiewerte | 20 | 5226 | float | RD | Reactive Energy (ind.), max. monthly value, apr., even year | varh
Energiewerte | 20 | 5228 | float | RD | Reactive Energy (ind.), max. monthly value, may., even year | varh
Energiewerte | 20 | 5230 | float | RD | Reactive Energy (ind.), max. monthly value, jun., even year | varh
Energiewerte | 20 | 5232 | float | RD | Reactive Energy (ind.), max. monthly value, jul., even year | varh
Energiewerte | 20 | 5234 | float | RD | Reactive Energy (ind.), max. monthly value, aug., even year | varh
Energiewerte | 20 | 5236 | float | RD | Reactive Energy (ind.), max. monthly value, sep., even year | varh
Energiewerte | 20 | 5238 | float | RD | Reactive Energy (ind.), max. monthly value, oct., even year | varh
Energiewerte | 20 | 5240 | float | RD | Reactive Energy (ind.), max. monthly value, nov., even year | varh
Energiewerte | 20 | 5242 | float | RD | Reactive Energy (ind.), max. monthly value, dec., even year | varh
Energiewerte | 20 | 5244 | float | RD | Reactive Energy (ind.), max. monthly value, jan., uneven year | varh
Energiewerte | 20 | 5246 | float | RD | Reactive Energy (ind.), max. monthly value, feb., uneven year | varh
Energiewerte | 20 | 5248 | float | RD | Reactive Energy (ind.), max. monthly value, mar., uneven year | varh
Energiewerte | 20 | 5250 | float | RD | Reactive Energy (ind.), max. monthly value, apr., uneven year | varh
Energiewerte | 20 | 5252 | float | RD | Reactive Energy (ind.), max. monthly value, may., uneven year | varh
Energiewerte | 20 | 5254 | float | RD | Reactive Energy (ind.), max. monthly value, jun., uneven year | varh
Energiewerte | 20 | 5256 | float | RD | Reactive Energy (ind.), max. monthly value, jul., uneven year | varh
Energiewerte | 20 | 5258 | float | RD | Reactive Energy (ind.), max. monthly value, aug., uneven year | varh
Energiewerte | 20 | 5260 | float | RD | Reactive Energy (ind.), max. monthly value, sep., uneven year | varh
Energiewerte | 20 | 5262 | float | RD | Reactive Energy (ind.), max. monthly value, oct., uneven year | varh
Energiewerte | 20 | 5264 | float | RD | Reactive Energy (ind.), max. monthly value, nov., uneven year | varh
Energiewerte | 20 | 5266 | float | RD | Reactive Energy (ind.), max. monthly value, dec., uneven year | varh
Energiewerte | 20 | 6000 | double | RD/WR | Active Energy L1, consumed | Wh | 0 | 3.403 e+38
Energiewerte | 20 | 6004 | double | RD/WR | Active Energy L2, consumed | Wh | 0 | 3.403 e+38
Energiewerte | 20 | 6008 | double | RD/WR | Active Energy L3, consumed | Wh | 0 | 3.403 e+38
Energiewerte | 20 | 6012 | double | RD/WR | Active Energy sum, consumed | Wh | 0 | 3.403 e+38
Energiewerte | 20 | 6016 | double | RD/WR | Active Energy L1, consumed, HT | Wh | 0 | 3.403 e+38
Energiewerte | 20 | 6020 | double | RD/WR | Active Energy L2, consumed, HT | Wh | 0 | 3.403 e+38
Energiewerte | 20 | 6024 | double | RD/WR | Active Energy L3, consumed, HT | Wh | 0 | 3.403 e+38
Energiewerte | 20 | 6028 | double | RD/WR | Active Energy sum, consumed, HT | Wh | 0 | 3.403 e+38
Energiewerte | 20 | 6032 | double | RD/WR | Active Energy L1, consumed, NT | Wh | 0 | 3.403 e+38
Energiewerte | 20 | 6036 | double | RD/WR | Active Energy L2, consumed, NT | Wh | 0 | 3.403 e+38
Energiewerte | 20 | 6040 | double | RD/WR | Active Energy L3, consumed, NT | Wh | 0 | 3.403 e+38
Energiewerte | 20 | 6044 | double | RD/WR | Active Energy sum, consumed, NT | Wh | 0 | 3.403 e+38
Energiewerte | 20 | 6048 | double | RD/WR | Apparent Energy L1 | VAh | 0 | 3.403 e+38
Energiewerte | 20 | 6052 | double | RD/WR | Apparent Energy L2 | VAh | 0 | 3.403 e+38
Energiewerte | 20 | 6056 | double | RD/WR | Apparent Energy L3 | VAh | 0 | 3.403 e+38
Energiewerte | 20 | 6060 | double | RD/WR | Apparent Energy, total | VAh | 0 | 3.403 e+38
Energiewerte | 20 | 6064 | double | RD/WR | Apparent Energy L1, HT | VAh | 0 | 3.403 e+38
Energiewerte | 20 | 6068 | double | RD/WR | Apparent Energy L2, HT | VAh | 0 | 3.403 e+38
Energiewerte | 20 | 6072 | double | RD/WR | Apparent Energy L3, HT | VAh | 0 | 3.403 e+38
Energiewerte | 20 | 6076 | double | RD/WR | Apparent Energy, total, HT | VAh | 0 | 3.403 e+38
Energiewerte | 20 | 6080 | double | RD/WR | Apparent Energy L1, NT | VAh | 0 | 3.403 e+38
Energiewerte | 20 | 6084 | double | RD/WR | Apparent Energy L2, NT | VAh | 0 | 3.403 e+38
Energiewerte | 20 | 6088 | double | RD/WR | Apparent Energy L3, NT | VAh | 0 | 3.403 e+38
Energiewerte | 20 | 6092 | double | RD/WR | Apparent Energy, total, NT | VAh | 0 | 3.403 e+38
Energiewerte | 20 | 6096 | double | RD/WR | Reactive Energy L1, inductive | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6100 | double | RD/WR | Reactive Energy L2, inductive | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6104 | double | RD/WR | Reactive Energy L3, inductive | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6108 | double | RD/WR | Reactive Energy sum, inductive | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6112 | double | RD/WR | Reactive Energy L1, inductive, HT | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6116 | double | RD/WR | Reactive Energy L2, inductive, HT | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6120 | double | RD/WR | Reactive Energy L3, inductive, HT | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6124 | double | RD/WR | Reactive Energy, total, inductive, HT | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6128 | double | RD/WR | Reactive Energy L1, inductive, NT | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6132 | double | RD/WR | Reactive Energy L2, inductive, NT | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6136 | double | RD/WR | Reactive Energy L3, inductive, NT | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6140 | double | RD/WR | Reactive Energy, total, inductive, NT | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6144 | double | RD/WR | Active Energy, delivered | Wh | 0 | 3.403 e+38
Energiewerte | 20 | 6148 | double | RD/WR | Active Energy L2, delivered | Wh | 0 | 3.403 e+38
Energiewerte | 20 | 6152 | double | RD/WR | Active Energy L3, delivered | Wh | 0 | 3.403 e+38
Energiewerte | 20 | 6156 | double | RD/WR | Active Energy sum, delivered | Wh | 0 | 3.403 e+38
Energiewerte | 20 | 6160 | double | RD/WR | Reactive Energy L1, capazitive | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6164 | double | RD/WR | Reactive Energy L2, capazitive | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6168 | double | RD/WR | Reactive Energy L3, capazitive | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6172 | double | RD/WR | Reactive Energy sum, capazitive | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6176 | double | RD/WR | Active Energy sum, without return travel block | Wh | 0 | 3.403 e+38
Energiewerte | 20 | 6180 | double | RD/WR | Reactive Energy sum, without return travel block | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6184 | double | RD/WR | Reactive Energy L1, inductive, consumed | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6188 | double | RD/WR | Reactive Energy L2, inductive, consumed | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6192 | double | RD/WR | Reactive Energy L3, inductive, consumed | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6196 | double | RD/WR | Reactive Energy sum, inductive, consumed | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6200 | double | RD/WR | Reactive Energy L1, capazitive, consumed | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6204 | double | RD/WR | Reactive Energy L2, capazitive, consumed | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6208 | double | RD/WR | Reactive Energy L3, capazitive, consumed | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6212 | double | RD/WR | Reactive Energy sum, capazitive, consumed | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6216 | double | RD/WR | Reactive Energy L1, inductive, delivered | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6220 | double | RD/WR | Reactive Energy L2, inductive, delivered | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6224 | double | RD/WR | Reactive Energy L3, inductive, delivered | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6228 | double | RD/WR | Reactive Energy sum, inductive, delivered | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6232 | double | RD/WR | Reactive Energy L1, capazitive, delivered | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6236 | double | RD/WR | Reactive Energy L2, capazitive, delivered | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6240 | double | RD/WR | Reactive Energy L3, capazitive, delivered | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6244 | double | RD/WR | Reactive Energy sum, capazitive, delivered | varh | 0 | 3.403 e+38
Energiewerte | 20 | 6248 | double | RD | Active Energy (consumed), max. monthly value, jan., even year | Wh
Energiewerte | 20 | 6252 | double | RD | Active Energy (consumed), max. monthly value, feb., even year | Wh
Energiewerte | 20 | 6256 | double | RD | Active Energy (consumed), max. monthly value, mar., even year | Wh
Energiewerte | 20 | 6260 | double | RD | Active Energy (consumed), max. monthly value, apr., even year | Wh
Energiewerte | 20 | 6264 | double | RD | Active Energy (consumed), max. monthly value, may., even year | Wh
Energiewerte | 20 | 6268 | double | RD | Active Energy (consumed), max. monthly value, jun., even year | Wh
Energiewerte | 20 | 6272 | double | RD | Active Energy (consumed), max. monthly value, jul., even year | Wh
Energiewerte | 20 | 6276 | double | RD | Active Energy (consumed), max. monthly value, aug., even year | Wh
Energiewerte | 20 | 6280 | double | RD | Active Energy (consumed), max. monthly value, sep., even year | Wh
Energiewerte | 20 | 6284 | double | RD | Active Energy (consumed), max. monthly value, oct., even year | Wh
Energiewerte | 20 | 6288 | double | RD | Active Energy (consumed), max. monthly value, nov., even year | Wh
Energiewerte | 20 | 6292 | double | RD | Active Energy (consumed), max. monthly value, dec., even year | Wh
Energiewerte | 20 | 6296 | double | RD | Active Energy (consumed), max. monthly value, jan., uneven year | Wh
Energiewerte | 20 | 6300 | double | RD | Active Energy (consumed), max. monthly value, feb., uneven year | Wh
Energiewerte | 20 | 6304 | double | RD | Active Energy (consumed), max. monthly value, mar., uneven year | Wh
Energiewerte | 20 | 6308 | double | RD | Active Energy (consumed), max. monthly value, apr., uneven year | Wh
Energiewerte | 20 | 6312 | double | RD | Active Energy (consumed), max. monthly value, may., uneven year | Wh
Energiewerte | 20 | 6316 | double | RD | Active Energy (consumed), max. monthly value, jun., uneven year | Wh
Energiewerte | 20 | 6320 | double | RD | Active Energy (consumed), max. monthly value, jul., uneven year | Wh
Energiewerte | 20 | 6324 | double | RD | Active Energy (consumed), max. monthly value, aug., uneven year | Wh
Energiewerte | 20 | 6328 | double | RD | Active Energy (consumed), max. monthly value, sep., uneven year | Wh
Energiewerte | 20 | 6332 | double | RD | Active Energy (consumed), max. monthly value, oct., uneven year | Wh
Energiewerte | 20 | 6336 | double | RD | Active Energy (consumed), max. monthly value, oct., uneven year | Wh
Energiewerte | 20 | 6340 | double | RD | Active Energy (consumed), max. monthly value, dec., uneven year | Wh
Energiewerte | 20 | 6344 | double | RD | Apparent Energy, max. monthly value, jan., even year | VAh
Energiewerte | 20 | 6348 | double | RD | Apparent Energy, max. monthly value, feb., even year | VAh
Energiewerte | 20 | 6352 | double | RD | Apparent Energy, max. monthly value, mar., even year | VAh
Energiewerte | 20 | 6356 | double | RD | Apparent Energy, max. monthly value, apr., even year | VAh
Energiewerte | 20 | 6360 | double | RD | Apparent Energy, max. monthly value, may., even year | VAh
Energiewerte | 20 | 6364 | double | RD | Apparent Energy, max. monthly value, jun., even year | VAh
Energiewerte | 20 | 6368 | double | RD | Apparent Energy, max. monthly value, jul., even year | VAh
Energiewerte | 20 | 6372 | double | RD | Apparent Energy, max. monthly value, aug., even year | VAh
Energiewerte | 20 | 6376 | double | RD | Apparent Energy, max. monthly value, sep., even year | VAh
Energiewerte | 20 | 6380 | double | RD | Apparent Energy, max. monthly value, oct., even year | VAh
Energiewerte | 20 | 6384 | double | RD | Apparent Energy, max. monthly value, nov., even year | VAh
Energiewerte | 20 | 6388 | double | RD | Apparent Energy, max. monthly value, dec., even year | VAh
Energiewerte | 20 | 6392 | double | RD | Apparent Energy, max. monthly value, jan., uneven year | VAh
Energiewerte | 20 | 6396 | double | RD | Apparent Energy, max. monthly value, feb., uneven year | VAh
Energiewerte | 20 | 6400 | double | RD | Apparent Energy, max. monthly value, mar., uneven year | VAh
Energiewerte | 20 | 6404 | double | RD | Apparent Energy, max. monthly value, apr., uneven year | VAh
Energiewerte | 20 | 6408 | double | RD | Apparent Energy, max. monthly value, may., uneven year | VAh
Energiewerte | 20 | 6412 | double | RD | Apparent Energy, max. monthly value, jun., uneven year | VAh
Energiewerte | 20 | 6416 | double | RD | Apparent Energy, max. monthly value, jul., uneven year | VAh
Energiewerte | 20 | 6420 | double | RD | Apparent Energy, max. monthly value, aug., uneven year | VAh
Energiewerte | 20 | 6424 | double | RD | Apparent Energy, max. monthly value, sep., uneven year | VAh
Energiewerte | 20 | 6428 | double | RD | Apparent Energy, max. monthly value, oct., uneven year | VAh
Energiewerte | 20 | 6432 | double | RD | Apparent Energy, max. monthly value, nov., uneven year | VAh
Energiewerte | 20 | 6436 | double | RD | Apparent Energy, max. monthly value, dec., uneven year | VAh
Energiewerte | 20 | 15000 | int | RD | Active Energy L1, consumed | Wh
Energiewerte | 20 | 15002 | int | RD | Active Energy L2, consumed | Wh
Energiewerte | 20 | 15004 | int | RD | Active Energy L3, consumed | Wh
Energiewerte | 20 | 15006 | int | RD | Active Energy sum, consumed | Wh
Energiewerte | 20 | 15008 | int | RD | Active Energy L1, consumed, HT | Wh
Energiewerte | 20 | 15010 | int | RD | Active Energy L2, consumed, HT | Wh
Energiewerte | 20 | 15012 | int | RD | Active Energy L3, consumed, HT | Wh
Energiewerte | 20 | 15014 | int | RD | Active Energy sum, consumed, HT | Wh
Energiewerte | 20 | 15016 | int | RD | Active Energy L1, consumed, NT | Wh
Energiewerte | 20 | 15018 | int | RD | Active Energy L2, consumed, NT | Wh
Energiewerte | 20 | 15020 | int | RD | Active Energy L3, consumed, NT | Wh
Energiewerte | 20 | 15022 | int | RD | Active Energy sum, consumed, NT | Wh
Energiewerte | 20 | 15024 | int | RD | Apparent Energy L1 | VAh
Energiewerte | 20 | 15026 | int | RD | Apparent Energy L2 | VAh
Energiewerte | 20 | 15028 | int | RD | Apparent Energy L3 | VAh
Energiewerte | 20 | 15030 | int | RD | Apparent Energy, total | VAh
Energiewerte | 20 | 15032 | int | RD | Apparent Energy L1, HT | VAh
Energiewerte | 20 | 15034 | int | RD | Apparent Energy L2, HT | VAh
Energiewerte | 20 | 15036 | int | RD | Apparent Energy L3, HT | VAh
Energiewerte | 20 | 15038 | int | RD | Apparent Energy, total, HT | VAh
Energiewerte | 20 | 15040 | int | RD | Apparent Energy L1, NT | VAh
Energiewerte | 20 | 15042 | int | RD | Apparent Energy L2, NT | VAh
Energiewerte | 20 | 15044 | int | RD | Apparent Energy L3, NT | VAh
Energiewerte | 20 | 15046 | int | RD | Apparent Energy, total, NT | VAh
Energiewerte | 20 | 15048 | int | RD | Reactive Energy L1, inductive | varh
Energiewerte | 20 | 15050 | int | RD | Reactive Energy L2, inductive | varh
Energiewerte | 20 | 15052 | int | RD | Reactive Energy L3, inductive | varh
Energiewerte | 20 | 15054 | int | RD | Reactive Energy sum, inductive | varh
Energiewerte | 20 | 15056 | int | RD | Reactive Energy L1, inductive, HT | varh
Energiewerte | 20 | 15058 | int | RD | Reactive Energy L2, inductive, HT | varh
Energiewerte | 20 | 15060 | int | RD | Reactive Energy L3, inductive, HT | varh
Energiewerte | 20 | 15062 | int | RD | Reactive Energy, total, inductive, HT | varh
Energiewerte | 20 | 15064 | int | RD | Reactive Energy L1, inductive, NT | varh
Energiewerte | 20 | 15066 | int | RD | Reactive Energy L2, inductive, NT | varh
Energiewerte | 20 | 15068 | int | RD | Reactive Energy L3, inductive, NT | varh
Energiewerte | 20 | 15070 | int | RD | Reactive Energy, total, inductive, NT | varh
Energiewerte | 20 | 15072 | int | RD | Active Energy L1, delivered | Wh
Energiewerte | 20 | 15074 | int | RD | Active Energy L2, delivered | Wh
Energiewerte | 20 | 15076 | int | RD | Active Energy L3, delivered | Wh
Energiewerte | 20 | 15078 | int | RD | Active Energy sum, delivered | Wh
Energiewerte | 20 | 15080 | int | RD | Reactive Energy L1, capazitive | varh
Energiewerte | 20 | 15082 | int | RD | Reactive Energy L2, capazitive | varh
Energiewerte | 20 | 15084 | int | RD | Reactive Energy L3, capazitive | varh
Energiewerte | 20 | 15086 | int | RD | Reactive Energy sum, capazitive | varh
Energiewerte | 20 | 15088 | int | RD | Active Energy sum, without return travel block | Wh
Energiewerte | 20 | 15090 | int | RD | Reactive Energy sum, without return travel block | varh
Energiewerte | 20 | 15092 | int | RD | Reactive Energy L1, inductive, consumed | varh
Energiewerte | 20 | 15094 | int | RD | Reactive Energy L2, inductive, consumed | varh
Energiewerte | 20 | 15096 | int | RD | Reactive Energy L3, inductive, consumed | varh
Energiewerte | 20 | 15098 | int | RD | Reactive Energy sum, inductive, consumed | varh
Energiewerte | 20 | 15100 | int | RD | Reactive Energy L1, capazitive, consumed | varh
Energiewerte | 20 | 15102 | int | RD | Reactive Energy L2, capazitive, consumed | varh
Energiewerte | 20 | 15104 | int | RD | Reactive Energy L3, capazitive, consumed | varh
Energiewerte | 20 | 15106 | int | RD | Reactive Energy sum, capazitive, consumed | varh
Energiewerte | 20 | 15108 | int | RD | Reactive Energy L1, inductive, delivered | varh
Energiewerte | 20 | 15110 | int | RD | Reactive Energy L2, inductive, delivered | varh
Energiewerte | 20 | 15112 | int | RD | Reactive Energy L3, inductive, delivered | varh
Energiewerte | 20 | 15114 | int | RD | Reactive Energy sum, inductive, delivered | varh
Energiewerte | 20 | 15116 | int | RD | Reactive Energy L1, capazitive, delivered | varh
Energiewerte | 20 | 15118 | int | RD | Reactive Energy L2, capazitive, delivered | varh
Energiewerte | 20 | 15120 | int | RD | Reactive Energy L3, capazitive, delivered | varh
Energiewerte | 20 | 15122 | int | RD | Reactive Energy sum, capazitive, delivered | varh
Energiewerte | 20 | 15124 | int | RD | Active Energy (consumed), max. monthly value, jan., even year | Wh
Energiewerte | 20 | 15126 | int | RD | Active Energy (consumed), max. monthly value, feb., even year | Wh
Energiewerte | 20 | 15128 | int | RD | Active Energy (consumed), max. monthly value, mar., even year | Wh
Energiewerte | 20 | 15130 | int | RD | Active Energy (consumed), max. monthly value, apr., even year | Wh
Energiewerte | 20 | 15132 | int | RD | Active Energy (consumed), max. monthly value, may., even year | Wh
Energiewerte | 20 | 15134 | int | RD | Active Energy (consumed), max. monthly value, jun., even year | Wh
Energiewerte | 20 | 15136 | int | RD | Active Energy (consumed), max. monthly value, jul., even year | Wh
Energiewerte | 20 | 15138 | int | RD | Active Energy (consumed), max. monthly value, aug., even year | Wh
Energiewerte | 20 | 15140 | int | RD | Active Energy (consumed), max. monthly value, sep., even year | Wh
Energiewerte | 20 | 15142 | int | RD | Active Energy (consumed), max. monthly value, oct., even year | Wh
Energiewerte | 20 | 15144 | int | RD | Active Energy (consumed), max. monthly value, nov., even year | Wh
Energiewerte | 20 | 15146 | int | RD | Active Energy (consumed), max. monthly value, dec., even year | Wh
Energiewerte | 20 | 15148 | int | RD | Active Energy (consumed), max. monthly value, jan., uneven year | Wh
Energiewerte | 20 | 15150 | int | RD | Active Energy (consumed), max. monthly value, feb., uneven year | Wh
Energiewerte | 20 | 15152 | int | RD | Active Energy (consumed), max. monthly value, mar., uneven year | Wh
Energiewerte | 20 | 15154 | int | RD | Active Energy (consumed), max. monthly value, apr., uneven year | Wh
Energiewerte | 20 | 15156 | int | RD | Active Energy (consumed), max. monthly value, may., uneven year | Wh
Energiewerte | 20 | 15158 | int | RD | Active Energy (consumed), max. monthly value, jun., uneven year | Wh
Energiewerte | 20 | 15160 | int | RD | Active Energy (consumed), max. monthly value, jul., uneven year | Wh
Energiewerte | 20 | 15162 | int | RD | Active Energy (consumed), max. monthly value, aug., uneven year | Wh
Energiewerte | 20 | 15164 | int | RD | Active Energy (consumed), max. monthly value, sep., uneven year | Wh
Energiewerte | 20 | 15166 | int | RD | Active Energy (consumed), max. monthly value, oct., uneven year | Wh
Energiewerte | 20 | 15168 | int | RD | Active Energy (consumed), max. monthly value, nov., uneven year | Wh
Energiewerte | 20 | 15170 | int | RD | Active Energy (consumed), max. monthly value, dec., uneven year | Wh
Energiewerte | 20 | 15192 | int | RD | Apparent Energy, max. monthly value, jan., even year | VAh
Energiewerte | 20 | 15194 | int | RD | Apparent Energy, max. monthly value, feb., even year | VAh
Energiewerte | 20 | 15196 | int | RD | Apparent Energy, max. monthly value, mar., even year | VAh
Energiewerte | 20 | 15198 | int | RD | Apparent Energy, max. monthly value, apr., even year | VAh
Energiewerte | 20 | 15200 | int | RD | Apparent Energy, max. monthly value, may., even year | VAh
Energiewerte | 20 | 15202 | int | RD | Apparent Energy, max. monthly value, jun., even year | VAh
Energiewerte | 20 | 15204 | int | RD | Apparent Energy, max. monthly value, jul., even year | VAh
Energiewerte | 20 | 15206 | int | RD | Apparent Energy, max. monthly value, aug., even year | VAh
Energiewerte | 20 | 15208 | int | RD | Apparent Energy, max. monthly value, sep., even year | VAh
Energiewerte | 20 | 15210 | int | RD | Apparent Energy, max. monthly value, oct., even year | VAh
Energiewerte | 20 | 15212 | int | RD | Apparent Energy, max. monthly value, nov., even year | VAh
Energiewerte | 20 | 15214 | int | RD | Apparent Energy, max. monthly value, dec., even year | VAh
Energiewerte | 20 | 15216 | int | RD | Apparent Energy, max. monthly value, jan., uneven year | VAh
Energiewerte | 20 | 15218 | int | RD | Apparent Energy, max. monthly value, feb., uneven year | VAh
Energiewerte | 20 | 15220 | int | RD | Apparent Energy, max. monthly value, mar., uneven year | VAh
Energiewerte | 20 | 15222 | int | RD | Apparent Energy, max. monthly value, apr., uneven year | VAh
Energiewerte | 20 | 15224 | int | RD | Apparent Energy, max. monthly value, may., uneven year | VAh
Energiewerte | 20 | 15226 | int | RD | Apparent Energy, max. monthly value, jun., uneven year | VAh
Energiewerte | 20 | 15228 | int | RD | Apparent Energy, max. monthly value, jul., uneven year | VAh
Energiewerte | 20 | 15230 | int | RD | Apparent Energy, max. monthly value, aug., uneven year | VAh
Energiewerte | 20 | 15232 | int | RD | Apparent Energy, max. monthly value, sep., uneven year | VAh
Energiewerte | 20 | 15234 | int | RD | Apparent Energy, max. monthly value, oct., uneven year | VAh
Energiewerte | 20 | 15236 | int | RD | Apparent Energy, max. monthly value, nov., uneven year | VAh
Energiewerte | 20 | 15238 | int | RD | Apparent Energy, max. monthly value, dec., uneven year | VAh
Energiewerte | 20 | 15240 | int | RD | Reactive Energy (ind.), max. monthly value, jan., even year | varh
Energiewerte | 20 | 15242 | int | RD | Reactive Energy (ind.), max. monthly value, feb., even year | varh
Energiewerte | 20 | 15244 | int | RD | Reactive Energy (ind.), max. monthly value, mar., even year | varh
Energiewerte | 20 | 15246 | int | RD | Reactive Energy (ind.), max. monthly value, apr., even year | varh
Energiewerte | 20 | 15248 | int | RD | Reactive Energy (ind.), max. monthly value, may., even year | varh
Energiewerte | 20 | 15250 | int | RD | Reactive Energy (ind.), max. monthly value, jun., even year | varh
Energiewerte | 20 | 15252 | int | RD | Reactive Energy (ind.), max. monthly value, jul., even year | varh
Energiewerte | 20 | 15254 | int | RD | Reactive Energy (ind.), max. monthly value, aug., even year | varh
Energiewerte | 20 | 15256 | int | RD | Reactive Energy (ind.), max. monthly value, sep., even year | varh
Energiewerte | 20 | 15258 | int | RD | Reactive Energy (ind.), max. monthly value, oct., even year | varh
Energiewerte | 20 | 15260 | int | RD | Reactive Energy (ind.), max. monthly value, nov., even year | varh
Energiewerte | 20 | 15262 | int | RD | Reactive Energy (ind.), max. monthly value, dec., even year | varh
Energiewerte | 20 | 15264 | int | RD | Reactive Energy (ind.), max. monthly value, jan., uneven year | varh
Energiewerte | 20 | 15266 | int | RD | Reactive Energy (ind.), max. monthly value, feb., uneven year | varh
Energiewerte | 20 | 15268 | int | RD | Reactive Energy (ind.), max. monthly value, mar., uneven year | varh
Energiewerte | 20 | 15270 | int | RD | Reactive Energy (ind.), max. monthly value, apr., uneven year | varh
Energiewerte | 20 | 15272 | int | RD | Reactive Energy (ind.), max. monthly value, may., uneven year | varh
Energiewerte | 20 | 15274 | int | RD | Reactive Energy (ind.), max. monthly value, jun., uneven year | varh
Energiewerte | 20 | 15276 | int | RD | Reactive Energy (ind.), max. monthly value, jul., uneven year | varh
Energiewerte | 20 | 15278 | int | RD | Reactive Energy (ind.), max. monthly value, aug., uneven year | varh
Energiewerte | 20 | 15280 | int | RD | Reactive Energy (ind.), max. monthly value, sep., uneven year | varh
Energiewerte | 20 | 15282 | int | RD | Reactive Energy (ind.), max. monthly value, oct., uneven year | varh
Energiewerte | 20 | 15284 | int | RD | Reactive Energy (ind.), max. monthly value, nov., uneven year | varh
Energiewerte | 20 | 15286 | int | RD | Reactive Energy (ind.), max. monthly value, dec., uneven year | varh
Digitale Ein- und Ausgänge | 25 | 806 | short | RD/WR | Trigger a power quality event by 806=1 |  | 0 | 1
Digitale Ein- und Ausgänge | 25 | 30046 | short | RD/WR | Function of digital input 1: 0 = S0 input (pulse counter) 1 = Tariff switch HT/NT 5 = Event trigger (PQ series only) - Rising edge 6 =Event trigger (PQ series only) - Falling Flank 7 = Event trigger (PQ series only) - Alternating flank |  | 0 | 7
Digitale Ein- und Ausgänge | 25 | 30047 | short | RD/WR | Function of digital input 2: 0 = S0 input (pulse counter) 1 = Clock sync - minutes 3 = Clock sync - hours 5 = Event trigger (PQ series only) - Rising edge 6 = Event trigger (PQ series only) - Falling flank 7 = Event trigger (PQ series only) - Alternating flank
Digitale Ein- und Ausgänge | 25 | 30048 | short | RD/WR | Function of digital input 3: 0 = S0 input (pulse counter) 4 = Drag indicator synchronisation 5 = Event triger (PQ series only) - Rising edge 6 = Event trigger (PQ series only) - Falling flank 7 = Event trigger - Alternating flank |  | 0 | 7
Digitale Ein- und Ausgänge | 25 | 30400 | short | RD | Digital I/O: status digital Input 1
Digitale Ein- und Ausgänge | 25 | 30401 | short | RD | Digital I/O: status digital Input 2
Digitale Ein- und Ausgänge | 25 | 30402 | short | RD | Digital I/O: status digital Input 3
Digitale Ein- und Ausgänge | 25 | 30406 | short | RD | Digital I/O: status digital Output 1
Digitale Ein- und Ausgänge | 25 | 30407 | short | RD | Digital I/O: status digital Output 2
Digitale Ein- und Ausgänge | 25 | 30408 | short | RD | Digital I/O: status digital Output 3
Digitale Ein- und Ausgänge | 25 | 30409 | short | RD/WR | Digital I/O: setting output 1 |  | 0 | 1
Digitale Ein- und Ausgänge | 25 | 30410 | short | RD/WR | Digital I/O: setting output 2 |  | 0 | 1
Digitale Ein- und Ausgänge | 25 | 30411 | short | RD/WR | Digital I/O: setting output 3 |  | 0 | 1
Digitale Ein- und Ausgänge | 25 | 30412 | float | RD | Digital I/O: power values S0 input 1
Digitale Ein- und Ausgänge | 25 | 30414 | float | RD | Digital I/O: power values S0 input 2
Digitale Ein- und Ausgänge | 25 | 30416 | float | RD | Digital I/O: power values S0 input 3
Digitale Ein- und Ausgänge | 25 | 30418 | long64 | RD/WR | Digital I/O: pulse counter, input 1 |  | 0 | 3.403 e+38
Digitale Ein- und Ausgänge | 25 | 30422 | long64 | RD/WR | Digital I/O: pulse counter, input 2 |  | 0 | 3.403 e+38
Digitale Ein- und Ausgänge | 25 | 30426 | long64 | RD/WR | Digital I/O: pulse counter, input 3 |  | 0 | 3.403 e+38
Digitale Ein- und Ausgänge | 25 | 30430 | int | RD | Digital I/O: pulse counter, input 1
Digitale Ein- und Ausgänge | 25 | 30432 | int | RD | Digital I/O: pulse counter, input 2
Digitale Ein- und Ausgänge | 25 | 30434 | int | RD | Digital I/O: pulse counter, input 3
Digitale Ein- und Ausgänge | 25 | 30436 | double | RD | Digital I/O: pulse count x scaling, input 1
Digitale Ein- und Ausgänge | 25 | 30440 | double | RD | Digital I/O: pulse count x scaling, input 2
Digitale Ein- und Ausgänge | 25 | 30444 | double | RD | Digital I/O: pulse count x scaling, input 3
Digitale Ein- und Ausgänge | 25 | 30448 | float | RD | Digital I/O: pulse count x scaling, input 1
Digitale Ein- und Ausgänge | 25 | 30450 | float | RD | Digital I/O: pulse count x scaling, input 2
Digitale Ein- und Ausgänge | 25 | 30452 | float | RD | Digital I/O: pulse count x scaling, input 3
Digitale Ein- und Ausgänge | 25 | 30565 | long64 | RD | Digital I/O: UTC timestamp, event 1, input 1 | s
Digitale Ein- und Ausgänge | 25 | 30569 | long64 | RD | Digital I/O: UTC timestamp, event 1, input 2 | s
Digitale Ein- und Ausgänge | 25 | 30573 | long64 | RD | Digital I/O: UTC timestamp, event 1, input 3 | s
Digitale Ein- und Ausgänge | 25 | 30577 | short | RD | Digital I/O: status, event 1, input 1 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30578 | short | RD | Digital I/O: status, event 1, input 2 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30579 | short | RD | Digital I/O: status, event 1, input 3 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30580 | long64 | RD | Digital I/O: UTC timestamp, event 2, input 1 | s
Digitale Ein- und Ausgänge | 25 | 30584 | long64 | RD | Digital I/O: UTC timestamp, event 2, input 2 | s
Digitale Ein- und Ausgänge | 25 | 30588 | long64 | RD | Digital I/O: UTC timestamp, event 2, input 3 | s
Digitale Ein- und Ausgänge | 25 | 30592 | short | RD | Digital I/O: status, event 2, input 1 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30593 | short | RD | Digital I/O: status, event 2, input 2 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30594 | short | RD | Digital I/O: status, event 2, input 3 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30595 | long64 | RD | Digital I/O: UTC timestamp, event 3, input 1 | s
Digitale Ein- und Ausgänge | 25 | 30599 | long64 | RD | Digital I/O: UTC timestamp, event 3, input 2 | s
Digitale Ein- und Ausgänge | 25 | 30603 | long64 | RD | Digital I/O: UTC timestamp, event 3, input 3 | s
Digitale Ein- und Ausgänge | 25 | 30607 | short | RD | Digital I/O: status, event 3, input 1 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30608 | short | RD | Digital I/O: status, event 3, input 2 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30609 | short | RD | Digital I/O: status, event 3, input 3 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30610 | long64 | RD | Digital I/O: UTC timestamp, event 4, input 1 | s
Digitale Ein- und Ausgänge | 25 | 30614 | long64 | RD | Digital I/O: UTC timestamp, event 4, input 2 | s
Digitale Ein- und Ausgänge | 25 | 30618 | long64 | RD | Digital I/O: UTC timestamp, event 4, input 3 | s
Digitale Ein- und Ausgänge | 25 | 30622 | short | RD | Digital I/O: status, event 4, input 1 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30623 | short | RD | Digital I/O: status, event 4, input 2 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30624 | short | RD | Digital I/O: status, event 4, input 3 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30625 | long64 | RD | Digital I/O: UTC timestamp, event 5, input 1 | s
Digitale Ein- und Ausgänge | 25 | 30629 | long64 | RD | Digital I/O: UTC timestamp, event 5, input 2 | s
Digitale Ein- und Ausgänge | 25 | 30633 | long64 | RD | Digital I/O: UTC timestamp, event 5, input 3 | s
Digitale Ein- und Ausgänge | 25 | 30637 | short | RD | Digital I/O: status, event 5, input 1 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30638 | short | RD | Digital I/O: status, event 5, input 2 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30639 | short | RD | Digital I/O: status, event 5, input 3 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30640 | long64 | RD | Digital I/O: UTC timestamp, event 6, input 1 | s
Digitale Ein- und Ausgänge | 25 | 30644 | long64 | RD | Digital I/O: UTC timestamp, event 6, input 2 | s
Digitale Ein- und Ausgänge | 25 | 30648 | long64 | RD | Digital I/O: UTC timestamp, event 6, input 3 | s
Digitale Ein- und Ausgänge | 25 | 30652 | short | RD | Digital I/O: status, event 6, input 1 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30653 | short | RD | Digital I/O: status, event 6, input 2 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30654 | short | RD | Digital I/O: status, event 6, input 3 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30655 | long64 | RD | Digital I/O: UTC timestamp, event 7, input 1 | s
Digitale Ein- und Ausgänge | 25 | 30659 | long64 | RD | Digital I/O: UTC timestamp, event 7, input 2 | s
Digitale Ein- und Ausgänge | 25 | 30663 | long64 | RD | Digital I/O: UTC timestamp, event 7, input 3 | s
Digitale Ein- und Ausgänge | 25 | 30667 | short | RD | Digital I/O: status, event 7, input 1 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30668 | short | RD | Digital I/O: status, event 7, input 2 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30669 | short | RD | Digital I/O: status, event 7, input 3 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30670 | long64 | RD | Digital I/O: UTC timestamp, event 8, input 1 | s
Digitale Ein- und Ausgänge | 25 | 30674 | long64 | RD | Digital I/O: UTC timestamp, event 8, input 2 | s
Digitale Ein- und Ausgänge | 25 | 30678 | long64 | RD | Digital I/O: UTC timestamp, event 8, input 3 | s
Digitale Ein- und Ausgänge | 25 | 30682 | short | RD | Digital I/O: status, event 8, input 1 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30683 | short | RD | Digital I/O: status, event 8, input 2 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30684 | short | RD | Digital I/O: status, event 8, input 3 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30685 | long64 | RD | Digital I/O: UTC timestamp, event 9, input 1 | s
Digitale Ein- und Ausgänge | 25 | 30689 | long64 | RD | Digital I/O: UTC timestamp, event 9, input 2 | s
Digitale Ein- und Ausgänge | 25 | 30693 | long64 | RD | Digital I/O: UTC timestamp, event 9, input 3 | s
Digitale Ein- und Ausgänge | 25 | 30697 | short | RD | Digital I/O: status, event 9, input 1 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30698 | short | RD | Digital I/O: status, event 9, input 2 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30699 | short | RD | Digital I/O: status, event 9, input 3 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30700 | long64 | RD | Digital I/O: UTC timestamp, event 10, input 1 | s
Digitale Ein- und Ausgänge | 25 | 30704 | long64 | RD | Digital I/O: UTC timestamp, event 10, input 2 | s
Digitale Ein- und Ausgänge | 25 | 30708 | long64 | RD | Digital I/O: UTC timestamp, event 10, input 3 | s
Digitale Ein- und Ausgänge | 25 | 30712 | short | RD | Digital I/O: status, event 10, input 1 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30713 | short | RD | Digital I/O: status, event 10, input 2 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30714 | short | RD | Digital I/O: status, event 10, input 3 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30715 | long64 | RD | Digital I/O: UTC timestamp, event 11, input 1 | s
Digitale Ein- und Ausgänge | 25 | 30719 | long64 | RD | Digital I/O: UTC timestamp, event 11, input 2 | s
Digitale Ein- und Ausgänge | 25 | 30723 | long64 | RD | Digital I/O: UTC timestamp, event 11, input 3 | s
Digitale Ein- und Ausgänge | 25 | 30727 | short | RD | Digital I/O: status, event 11, input 1 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30728 | short | RD | Digital I/O: status, event 11, input 2 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30729 | short | RD | Digital I/O: status, event 11, input 3 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30730 | long64 | RD | Digital I/O: UTC timestamp, event 12, input 1 | s
Digitale Ein- und Ausgänge | 25 | 30734 | long64 | RD | Digital I/O: UTC timestamp, event 12, input 2 | s
Digitale Ein- und Ausgänge | 25 | 30738 | long64 | RD | Digital I/O: UTC timestamp, event 12, input 3 | s
Digitale Ein- und Ausgänge | 25 | 30742 | short | RD | Digital I/O: status, event 12, input 1 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30743 | short | RD | Digital I/O: status, event 12, input 2 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30744 | short | RD | Digital I/O: status, event 12, input 3 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30745 | long64 | RD | Digital I/O: UTC timestamp, event 13, input 1 | s
Digitale Ein- und Ausgänge | 25 | 30749 | long64 | RD | Digital I/O: UTC timestamp, event 13, input 2 | s
Digitale Ein- und Ausgänge | 25 | 30753 | long64 | RD | Digital I/O: UTC timestamp, event 13, input 3 | s
Digitale Ein- und Ausgänge | 25 | 30757 | short | RD | Digital I/O: status, event 13, input 1 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30758 | short | RD | Digital I/O: status, event 13, input 2 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30759 | short | RD | Digital I/O: status, event 13, input 3 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30760 | long64 | RD | Digital I/O: UTC timestamp, event 14, input 1 | s
Digitale Ein- und Ausgänge | 25 | 30764 | long64 | RD | Digital I/O: UTC timestamp, event 14, input 2 | s
Digitale Ein- und Ausgänge | 25 | 30768 | long64 | RD | Digital I/O: UTC timestamp, event 14, input 3 | s
Digitale Ein- und Ausgänge | 25 | 30772 | short | RD | Digital I/O: status, event 14, input 1 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30773 | short | RD | Digital I/O: status, event 14, input 2 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30774 | short | RD | Digital I/O: status, event 14, input 3 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30775 | long64 | RD | Digital I/O: UTC timestamp, event 15, input 1 | s
Digitale Ein- und Ausgänge | 25 | 30779 | long64 | RD | Digital I/O: UTC timestamp, event 15, input 2 | s
Digitale Ein- und Ausgänge | 25 | 30783 | long64 | RD | Digital I/O: UTC timestamp, event 15, input 3 | s
Digitale Ein- und Ausgänge | 25 | 30787 | short | RD | Digital I/O: status, event 15, input 1 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30788 | short | RD | Digital I/O: status, event 15, input 2 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30789 | short | RD | Digital I/O: status, event 15, input 3 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30790 | long64 | RD | Digital I/O: UTC timestamp, event 16, input 1 | s
Digitale Ein- und Ausgänge | 25 | 30794 | long64 | RD | Digital I/O: UTC timestamp, event 16, input 2 | s
Digitale Ein- und Ausgänge | 25 | 30798 | long64 | RD | Digital I/O: UTC timestamp, event 16, input 3 | s
Digitale Ein- und Ausgänge | 25 | 30802 | short | RD | Digital I/O: status, event 16, input 1 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30803 | short | RD | Digital I/O: status, event 16, input 2 (0=off, 1=on)
Digitale Ein- und Ausgänge | 25 | 30804 | short | RD | Digital I/O: status, event 16, input 3 (0=off, 1=on)
Vergleichergruppen | 30 | 32500 | char | RD | PQ-L series: comparator group 1 comparator A
Vergleichergruppen | 30 | 32501 | char | RD | PQ-L series: comparator group 1 comparator B
Vergleichergruppen | 30 | 32502 | char | RD | PQ-L series: comparator group 1 comparator C
Vergleichergruppen | 30 | 32503 | char | RD | PQ-L series: comparator group 1 comparator D
Vergleichergruppen | 30 | 32504 | char | RD | PQ-L series: comparator group 1 comparator E
Vergleichergruppen | 30 | 32505 | char | RD | PQ-L series: comparator group 1 comparator F
Vergleichergruppen | 30 | 32506 | char | RD | PQ-L series: comparator group 1 comparator G
Vergleichergruppen | 30 | 32507 | char | RD | PQ-L series: comparator group 1 comparator H
Vergleichergruppen | 30 | 32508 | char | RD | PQ-L series: comparator group 1 comparator I
Vergleichergruppen | 30 | 32509 | char | RD | PQ-L series: comparator group 1 comparator J
Vergleichergruppen | 30 | 32510 | char | RD | PQ-L series: comparator group 1 group comparator 1
Vergleichergruppen | 30 | 32511 | char | RD | PQ-L series: comparator group 2 comparator A
Vergleichergruppen | 30 | 32512 | char | RD | PQ-L series: comparator group 2 comparator B
Vergleichergruppen | 30 | 32513 | char | RD | PQ-L series: comparator group 2 comparator C
Vergleichergruppen | 30 | 32514 | char | RD | PQ-L series: comparator group 2 comparator D
Vergleichergruppen | 30 | 32515 | char | RD | PQ-L series: comparator group 2 comparator E
Vergleichergruppen | 30 | 32516 | char | RD | PQ-L series: comparator group 2 comparator F
Vergleichergruppen | 30 | 32517 | char | RD | PQ-L series: comparator group 2 comparator G
Vergleichergruppen | 30 | 32518 | char | RD | PQ-L series: comparator group 2 comparator H
Vergleichergruppen | 30 | 32519 | char | RD | PQ-L series: comparator group 2 comparator I
Vergleichergruppen | 30 | 32520 | char | RD | PQ-L series: comparator group 2 comparator J
Vergleichergruppen | 30 | 32521 | char | RD | PQ-L series: comparator group 2 group comparator 2
Vergleichergruppen | 30 | 32522 | char | RD | PQ-L series: comparator group 3 comparator A
Vergleichergruppen | 30 | 32523 | char | RD | PQ-L series: comparator group 3 comparator B
Vergleichergruppen | 30 | 32524 | char | RD | PQ-L series: comparator group 3 comparator C
Vergleichergruppen | 30 | 32525 | char | RD | PQ-L series: comparator group 3 comparator D
Vergleichergruppen | 30 | 32526 | char | RD | PQ-L series: comparator group 3 comparator E
Vergleichergruppen | 30 | 32527 | char | RD | PQ-L series: comparator group 3 comparator F
Vergleichergruppen | 30 | 32528 | char | RD | PQ-L series: comparator group 3 comparator G
Vergleichergruppen | 30 | 32529 | char | RD | PQ-L series: comparator group 3 comparator H
Vergleichergruppen | 30 | 32530 | char | RD | PQ-L series: comparator group 3 comparator I
Vergleichergruppen | 30 | 32531 | char | RD | PQ-L series: comparator group 3 comparator J
Vergleichergruppen | 30 | 32532 | char | RD | PQ-L series: comparator group 3 group comparator 3
Vergleichergruppen | 30 | 32533 | char | RD | PQ-L series: comparator group 4 comparator A
Vergleichergruppen | 30 | 32534 | char | RD | PQ-L series: comparator group 4 comparator B
Vergleichergruppen | 30 | 32535 | char | RD | PQ-L series: comparator group 4 comparator C
Vergleichergruppen | 30 | 32536 | char | RD | PQ-L series: comparator group 4 comparator D
Vergleichergruppen | 30 | 32537 | char | RD | PQ-L series: comparator group 4 comparator E
Vergleichergruppen | 30 | 32538 | char | RD | PQ-L series: comparator group 4 comparator F
Vergleichergruppen | 30 | 32539 | char | RD | PQ-L series: comparator group 4 comparator G
Vergleichergruppen | 30 | 32540 | char | RD | PQ-L series: comparator group 4 comparator H
Vergleichergruppen | 30 | 32541 | char | RD | PQ-L series: comparator group 4 comparator I
Vergleichergruppen | 30 | 32542 | char | RD | PQ-L series: comparator group 4 comparator J
Vergleichergruppen | 30 | 32543 | char | RD | PQ-L series: comparator group 4 group comparator 4
Vergleichergruppen | 30 | 32544 | char | RD | PQ-L series: comparator group 5 comparator A
Vergleichergruppen | 30 | 32545 | char | RD | PQ-L series: comparator group 5 comparator B
Vergleichergruppen | 30 | 32546 | char | RD | PQ-L series: comparator group 5 comparator C
Vergleichergruppen | 30 | 32547 | char | RD | PQ-L series: comparator group 5 comparator D
Vergleichergruppen | 30 | 32548 | char | RD | PQ-L series: comparator group 5 comparator E
Vergleichergruppen | 30 | 32549 | char | RD | PQ-L series: comparator group 5 comparator F
Vergleichergruppen | 30 | 32550 | char | RD | PQ-L series: comparator group 5 comparator G
Vergleichergruppen | 30 | 32551 | char | RD | PQ-L series: comparator group 5 comparator H
Vergleichergruppen | 30 | 32552 | char | RD | PQ-L series: comparator group 5 comparator I
Vergleichergruppen | 30 | 32553 | char | RD | PQ-L series: comparator group 5 comparator J
Vergleichergruppen | 30 | 32554 | char | RD | PQ-L series: comparator group 5 group comparator 5
Ereignisse, letztes Ereignis über Modbus auslesen | 31 | 16643 | ushort | RD | Last event phase (consider together with 16644): 0= Phase 1 (U or I), DigIn 1, Modbus event, 1= Phase 2 (U or I), DigIn 2 2= Phase 3 (U or I), DigIn 3 3= Multievent: At least in 2 phases for U and I events. With a frequency event, all 3 phases are always affected. 4= Event I4 5= Event I5 6= Event I6 If the device does not have an event, a 0 is displayed here.
Ereignisse, letztes Ereignis über Modbus auslesen | 31 | 16644 | short | RD | Event type: -1= No event 0= IMAX_EVENT - Overcurrent 1= UMAX_EVENT - Overvoltage 2= UMIN_EVENT - Undervoltage 3= UOFF_EVENT - Voltage interruption 4= EXT_DIGIN - External event (dig. input) 5= EXT_MODBUS - External event (Modbus) 6= RVC_EVENT - Fast voltage change 7= FREQ_OVER_EVENT - Overfrequency 8= FREQ_UNDER_EVENT - Underfrequency 9= IMAX_RCM_EVENT - Overcurrent event in the analog RCM inputs (only in meters with module)
Ereignisse, letztes Ereignis über Modbus auslesen | 31 | 16645 | ulong64 | RD | Event start time, UTC timestamp (resolution in ns) 0= no event
Ereignisse, letztes Ereignis über Modbus auslesen | 31 | 16649 | uint | RD | Event duration (end time - start time in ns), 0= Event type EXT_DIGIN or EXT_MODBUS (external events do not have an end time) 0= No events (with simultaneous „Value -1 = No event“ for the event type)
Ereignisse, letztes Ereignis über Modbus auslesen | 31 | 16651 | float | RD | Measured value of the event 0= Event type EXT_DIGIN and EXT_MODBUS (external events do not have any measured values) -1= No event
Fourieranalyse, Messwerte | 41 | 1058 | float | RD | Fourier analysis: 1. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 1060 | float | RD | Fourier analysis: 3. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 1062 | float | RD | Fourier analysis: 5. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 1064 | float | RD | Fourier analysis: 7. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 1066 | float | RD | Fourier analysis: 9. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 1068 | float | RD | Fourier analysis: 11. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 1070 | float | RD | Fourier analysis: 13. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 1072 | float | RD | Fourier analysis: 15. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 1074 | float | RD | Fourier analysis: 17. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 1076 | float | RD | Fourier analysis: 19. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 1078 | float | RD | Fourier analysis: 21. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 1080 | float | RD | Fourier analysis: 23. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 1082 | float | RD | Fourier analysis: 25. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 1084 | float | RD | Fourier analysis: 1. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 1086 | float | RD | Fourier analysis: 3. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 1088 | float | RD | Fourier analysis: 5. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 1090 | float | RD | Fourier analysis: 7. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 1092 | float | RD | Fourier analysis: 9. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 1094 | float | RD | Fourier analysis: 11. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 1096 | float | RD | Fourier analysis: 13. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 1098 | float | RD | Fourier analysis: 15. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 1100 | float | RD | Fourier analysis: 17. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 1102 | float | RD | Fourier analysis: 19. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 1104 | float | RD | Fourier analysis: 21. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 1106 | float | RD | Fourier analysis: 23. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 1108 | float | RD | Fourier analysis: 25. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 1110 | float | RD | Fourier analysis: 1. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 1112 | float | RD | Fourier analysis: 3. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 1114 | float | RD | Fourier analysis: 5. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 1116 | float | RD | Fourier analysis: 7. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 1118 | float | RD | Fourier analysis: 9. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 1120 | float | RD | Fourier analysis: 11. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 1122 | float | RD | Fourier analysis: 13. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 1124 | float | RD | Fourier analysis: 15. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 1126 | float | RD | Fourier analysis: 17. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 1128 | float | RD | Fourier analysis: 19. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 1130 | float | RD | Fourier analysis: 21. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 1132 | float | RD | Fourier analysis: 23. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 1134 | float | RD | Fourier analysis: 25. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 1136 | float | RD | Fourier analysis: 1. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 1138 | float | RD | Fourier analysis: 3. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 1140 | float | RD | Fourier analysis: 5. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 1142 | float | RD | Fourier analysis: 7. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 1144 | float | RD | Fourier analysis: 9. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 1146 | float | RD | Fourier analysis: 11. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 1148 | float | RD | Fourier analysis: 13. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 1150 | float | RD | Fourier analysis: 15. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 1152 | float | RD | Fourier analysis: 17. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 1154 | float | RD | Fourier analysis: 19. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 1156 | float | RD | Fourier analysis: 21. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 1158 | float | RD | Fourier analysis: 23. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 1160 | float | RD | Fourier analysis: 25. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 1162 | float | RD | Fourier analysis: 1. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 1164 | float | RD | Fourier analysis: 3. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 1166 | float | RD | Fourier analysis: 5. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 1168 | float | RD | Fourier analysis: 7. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 1170 | float | RD | Fourier analysis: 9. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 1172 | float | RD | Fourier analysis: 11. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 1174 | float | RD | Fourier analysis: 13. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 1176 | float | RD | Fourier analysis: 15. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 1178 | float | RD | Fourier analysis: 17. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 1180 | float | RD | Fourier analysis: 19. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 1182 | float | RD | Fourier analysis: 21. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 1184 | float | RD | Fourier analysis: 23. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 1186 | float | RD | Fourier analysis: 25. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 1188 | float | RD | Fourier analysis: 1. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 1190 | float | RD | Fourier analysis: 3. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 1192 | float | RD | Fourier analysis: 5. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 1194 | float | RD | Fourier analysis: 7. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 1196 | float | RD | Fourier analysis: 9. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 1198 | float | RD | Fourier analysis: 11. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 1200 | float | RD | Fourier analysis: 13. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 1202 | float | RD | Fourier analysis: 15. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 1204 | float | RD | Fourier analysis: 17. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 1206 | float | RD | Fourier analysis: 19. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 1208 | float | RD | Fourier analysis: 21. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 1210 | float | RD | Fourier analysis: 23. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 1212 | float | RD | Fourier analysis: 25. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8000 | float | RD | Fourier analysis: 1. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8002 | float | RD | Fourier analysis: 2. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8004 | float | RD | Fourier analysis: 3. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8006 | float | RD | Fourier analysis: 4. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8008 | float | RD | Fourier analysis: 5. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8010 | float | RD | Fourier analysis: 6. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8012 | float | RD | Fourier analysis: 7. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8014 | float | RD | Fourier analysis: 8. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8016 | float | RD | Fourier analysis: 9. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8018 | float | RD | Fourier analysis: 10. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8020 | float | RD | Fourier analysis: 11. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8022 | float | RD | Fourier analysis: 12. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8024 | float | RD | Fourier analysis: 13. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8026 | float | RD | Fourier analysis: 14. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8028 | float | RD | Fourier analysis: 15. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8030 | float | RD | Fourier analysis: 16. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8032 | float | RD | Fourier analysis: 17. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8034 | float | RD | Fourier analysis: 18. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8036 | float | RD | Fourier analysis: 19. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8038 | float | RD | Fourier analysis: 20. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8040 | float | RD | Fourier analysis: 21. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8042 | float | RD | Fourier analysis: 22. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8044 | float | RD | Fourier analysis: 23. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8046 | float | RD | Fourier analysis: 24. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8048 | float | RD | Fourier analysis: 25. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8050 | float | RD | Fourier analysis: 26. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8052 | float | RD | Fourier analysis: 27. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8054 | float | RD | Fourier analysis: 28. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8056 | float | RD | Fourier analysis: 29. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8058 | float | RD | Fourier analysis: 30. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8060 | float | RD | Fourier analysis: 31. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8062 | float | RD | Fourier analysis: 32. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8064 | float | RD | Fourier analysis: 33. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8066 | float | RD | Fourier analysis: 34. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8068 | float | RD | Fourier analysis: 35. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8070 | float | RD | Fourier analysis: 36. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8072 | float | RD | Fourier analysis: 37. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8074 | float | RD | Fourier analysis: 38. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8076 | float | RD | Fourier analysis: 39. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8078 | float | RD | Fourier analysis: 40. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 8080 | float | RD | Fourier analysis: 1. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8082 | float | RD | Fourier analysis: 2. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8084 | float | RD | Fourier analysis: 3. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8086 | float | RD | Fourier analysis: 4. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8088 | float | RD | Fourier analysis: 5. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8090 | float | RD | Fourier analysis: 6. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8092 | float | RD | Fourier analysis: 7. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8094 | float | RD | Fourier analysis: 8. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8096 | float | RD | Fourier analysis: 9. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8098 | float | RD | Fourier analysis: 10. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8100 | float | RD | Fourier analysis: 11. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8102 | float | RD | Fourier analysis: 12. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8104 | float | RD | Fourier analysis: 13. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8106 | float | RD | Fourier analysis: 14. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8108 | float | RD | Fourier analysis: 15. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8110 | float | RD | Fourier analysis: 16. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8112 | float | RD | Fourier analysis: 17. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8114 | float | RD | Fourier analysis: 18. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8116 | float | RD | Fourier analysis: 19. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8118 | float | RD | Fourier analysis: 20. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8120 | float | RD | Fourier analysis: 21. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8122 | float | RD | Fourier analysis: 22. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8124 | float | RD | Fourier analysis: 23. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8126 | float | RD | Fourier analysis: 24. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8128 | float | RD | Fourier analysis: 25. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8130 | float | RD | Fourier analysis: 26. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8132 | float | RD | Fourier analysis: 27. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8134 | float | RD | Fourier analysis: 28. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8136 | float | RD | Fourier analysis: 29. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8138 | float | RD | Fourier analysis: 30. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8140 | float | RD | Fourier analysis: 31. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8142 | float | RD | Fourier analysis: 32. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8144 | float | RD | Fourier analysis: 33. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8146 | float | RD | Fourier analysis: 34. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8148 | float | RD | Fourier analysis: 35. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8150 | float | RD | Fourier analysis: 36. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8152 | float | RD | Fourier analysis: 37. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8154 | float | RD | Fourier analysis: 38. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8156 | float | RD | Fourier analysis: 39. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8158 | float | RD | Fourier analysis: 40. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 8160 | float | RD | Fourier analysis: 1. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8162 | float | RD | Fourier analysis: 2. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8164 | float | RD | Fourier analysis: 3. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8166 | float | RD | Fourier analysis: 4. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8168 | float | RD | Fourier analysis: 5. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8170 | float | RD | Fourier analysis: 6. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8172 | float | RD | Fourier analysis: 7. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8174 | float | RD | Fourier analysis: 8. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8176 | float | RD | Fourier analysis: 9. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8178 | float | RD | Fourier analysis: 10. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8180 | float | RD | Fourier analysis: 11. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8182 | float | RD | Fourier analysis: 12. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8184 | float | RD | Fourier analysis: 13. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8186 | float | RD | Fourier analysis: 14. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8188 | float | RD | Fourier analysis: 15. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8190 | float | RD | Fourier analysis: 16. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8192 | float | RD | Fourier analysis: 17. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8194 | float | RD | Fourier analysis: 18. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8196 | float | RD | Fourier analysis: 19. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8198 | float | RD | Fourier analysis: 20. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8200 | float | RD | Fourier analysis: 21. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8202 | float | RD | Fourier analysis: 22. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8204 | float | RD | Fourier analysis: 23. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8206 | float | RD | Fourier analysis: 24. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8208 | float | RD | Fourier analysis: 25. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8210 | float | RD | Fourier analysis: 26. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8212 | float | RD | Fourier analysis: 27. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8214 | float | RD | Fourier analysis: 28. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8216 | float | RD | Fourier analysis: 29. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8218 | float | RD | Fourier analysis: 30. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8220 | float | RD | Fourier analysis: 31. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8222 | float | RD | Fourier analysis: 32. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8224 | float | RD | Fourier analysis: 33. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8226 | float | RD | Fourier analysis: 34. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8228 | float | RD | Fourier analysis: 35. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8230 | float | RD | Fourier analysis: 36. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8232 | float | RD | Fourier analysis: 37. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8234 | float | RD | Fourier analysis: 38. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8236 | float | RD | Fourier analysis: 39. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8238 | float | RD | Fourier analysis: 40. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 8240 | float | RD | Fourier analysis: 1. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8242 | float | RD | Fourier analysis: 2. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8244 | float | RD | Fourier analysis: 3. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8246 | float | RD | Fourier analysis: 4. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8248 | float | RD | Fourier analysis: 5. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8250 | float | RD | Fourier analysis: 6. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8252 | float | RD | Fourier analysis: 7. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8254 | float | RD | Fourier analysis: 8. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8256 | float | RD | Fourier analysis: 9. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8258 | float | RD | Fourier analysis: 10. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8260 | float | RD | Fourier analysis: 11. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8262 | float | RD | Fourier analysis: 12. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8264 | float | RD | Fourier analysis: 13. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8266 | float | RD | Fourier analysis: 14. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8268 | float | RD | Fourier analysis: 15. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8270 | float | RD | Fourier analysis: 16. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8272 | float | RD | Fourier analysis: 17. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8274 | float | RD | Fourier analysis: 18. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8276 | float | RD | Fourier analysis: 19. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8278 | float | RD | Fourier analysis: 20. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8280 | float | RD | Fourier analysis: 21. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8282 | float | RD | Fourier analysis: 22. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8284 | float | RD | Fourier analysis: 23. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8286 | float | RD | Fourier analysis: 24. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8288 | float | RD | Fourier analysis: 25. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8290 | float | RD | Fourier analysis: 26. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8292 | float | RD | Fourier analysis: 27. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8294 | float | RD | Fourier analysis: 28. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8296 | float | RD | Fourier analysis: 29. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8298 | float | RD | Fourier analysis: 30. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8300 | float | RD | Fourier analysis: 31. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8302 | float | RD | Fourier analysis: 32. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8304 | float | RD | Fourier analysis: 33. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8306 | float | RD | Fourier analysis: 34. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8308 | float | RD | Fourier analysis: 35. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8310 | float | RD | Fourier analysis: 36. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8312 | float | RD | Fourier analysis: 37. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8314 | float | RD | Fourier analysis: 38. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8316 | float | RD | Fourier analysis: 39. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8318 | float | RD | Fourier analysis: 40. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 8320 | float | RD | Fourier analysis: 1. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8322 | float | RD | Fourier analysis: 2. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8324 | float | RD | Fourier analysis: 3. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8326 | float | RD | Fourier analysis: 4. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8328 | float | RD | Fourier analysis: 5. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8330 | float | RD | Fourier analysis: 6. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8332 | float | RD | Fourier analysis: 7. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8334 | float | RD | Fourier analysis: 8. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8336 | float | RD | Fourier analysis: 9. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8338 | float | RD | Fourier analysis: 10. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8340 | float | RD | Fourier analysis: 11. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8342 | float | RD | Fourier analysis: 12. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8344 | float | RD | Fourier analysis: 13. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8346 | float | RD | Fourier analysis: 14. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8348 | float | RD | Fourier analysis: 15. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8350 | float | RD | Fourier analysis: 16. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8352 | float | RD | Fourier analysis: 17. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8354 | float | RD | Fourier analysis: 18. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8356 | float | RD | Fourier analysis: 19. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8358 | float | RD | Fourier analysis: 20. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8360 | float | RD | Fourier analysis: 21. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8362 | float | RD | Fourier analysis: 22. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8364 | float | RD | Fourier analysis: 23. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8366 | float | RD | Fourier analysis: 24. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8368 | float | RD | Fourier analysis: 25. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8370 | float | RD | Fourier analysis: 26. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8372 | float | RD | Fourier analysis: 27. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8374 | float | RD | Fourier analysis: 28. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8376 | float | RD | Fourier analysis: 29. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8378 | float | RD | Fourier analysis: 30. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8380 | float | RD | Fourier analysis: 31. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8382 | float | RD | Fourier analysis: 32. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8384 | float | RD | Fourier analysis: 33. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8386 | float | RD | Fourier analysis: 34. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8388 | float | RD | Fourier analysis: 35. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8390 | float | RD | Fourier analysis: 36. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8392 | float | RD | Fourier analysis: 37. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8394 | float | RD | Fourier analysis: 38. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8396 | float | RD | Fourier analysis: 39. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8398 | float | RD | Fourier analysis: 40. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 8400 | float | RD | Fourier analysis: 1. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8402 | float | RD | Fourier analysis: 2. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8404 | float | RD | Fourier analysis: 3. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8406 | float | RD | Fourier analysis: 4. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8408 | float | RD | Fourier analysis: 5. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8410 | float | RD | Fourier analysis: 6. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8412 | float | RD | Fourier analysis: 7. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8414 | float | RD | Fourier analysis: 8. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8416 | float | RD | Fourier analysis: 9. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8418 | float | RD | Fourier analysis: 10. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8420 | float | RD | Fourier analysis: 11. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8422 | float | RD | Fourier analysis: 12. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8424 | float | RD | Fourier analysis: 13. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8426 | float | RD | Fourier analysis: 14. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8428 | float | RD | Fourier analysis: 15. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8430 | float | RD | Fourier analysis: 16. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8432 | float | RD | Fourier analysis: 17. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8434 | float | RD | Fourier analysis: 18. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8436 | float | RD | Fourier analysis: 19. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8438 | float | RD | Fourier analysis: 20. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8440 | float | RD | Fourier analysis: 21. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8442 | float | RD | Fourier analysis: 22. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8444 | float | RD | Fourier analysis: 23. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8446 | float | RD | Fourier analysis: 24. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8448 | float | RD | Fourier analysis: 25. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8450 | float | RD | Fourier analysis: 26. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8452 | float | RD | Fourier analysis: 27. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8454 | float | RD | Fourier analysis: 28. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8456 | float | RD | Fourier analysis: 29. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8458 | float | RD | Fourier analysis: 30. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8460 | float | RD | Fourier analysis: 31. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8462 | float | RD | Fourier analysis: 32. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8464 | float | RD | Fourier analysis: 33. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8466 | float | RD | Fourier analysis: 34. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8468 | float | RD | Fourier analysis: 35. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8470 | float | RD | Fourier analysis: 36. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8472 | float | RD | Fourier analysis: 37. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8474 | float | RD | Fourier analysis: 38. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8476 | float | RD | Fourier analysis: 39. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 8478 | float | RD | Fourier analysis: 40. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 11029 | short (x10) | RD | Fourier analysis: 1. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 11030 | short (x10) | RD | Fourier analysis: 3. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 11031 | short (x10) | RD | Fourier analysis: 5. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 11032 | short (x10) | RD | Fourier analysis: 7. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 11033 | short (x10) | RD | Fourier analysis: 9. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 11034 | short (x10) | RD | Fourier analysis: 11. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 11035 | short (x10) | RD | Fourier analysis: 13. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 11036 | short (x10) | RD | Fourier analysis: 15. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 11037 | short (x10) | RD | Fourier analysis: 17. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 11038 | short (x10) | RD | Fourier analysis: 19. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 11039 | short (x10) | RD | Fourier analysis: 21. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 11040 | short (x10) | RD | Fourier analysis: 23. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 11041 | short (x10) | RD | Fourier analysis: 25. harmonic voltage L1 | V
Fourieranalyse, Messwerte | 41 | 11042 | short (x10) | RD | Fourier analysis: 1. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 11043 | short (x10) | RD | Fourier analysis: 3. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 11044 | short (x10) | RD | Fourier analysis: 5. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 11045 | short (x10) | RD | Fourier analysis: 7. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 11046 | short (x10) | RD | Fourier analysis: 9. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 11047 | short (x10) | RD | Fourier analysis: 11. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 11048 | short (x10) | RD | Fourier analysis: 13. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 11049 | short (x10) | RD | Fourier analysis: 15. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 11050 | short (x10) | RD | Fourier analysis: 17. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 11051 | short (x10) | RD | Fourier analysis: 19. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 11052 | short (x10) | RD | Fourier analysis: 21. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 11053 | short (x10) | RD | Fourier analysis: 23. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 11054 | short (x10) | RD | Fourier analysis: 25. harmonic voltage L2 | V
Fourieranalyse, Messwerte | 41 | 11055 | short (x10) | RD | Fourier analysis: 1. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 11056 | short (x10) | RD | Fourier analysis: 3. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 11057 | short (x10) | RD | Fourier analysis: 5. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 11058 | short (x10) | RD | Fourier analysis: 7. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 11059 | short (x10) | RD | Fourier analysis: 9. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 11060 | short (x10) | RD | Fourier analysis: 11. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 11061 | short (x10) | RD | Fourier analysis: 13. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 11062 | short (x10) | RD | Fourier analysis: 15. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 11063 | short (x10) | RD | Fourier analysis: 17. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 11064 | short (x10) | RD | Fourier analysis: 19. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 11065 | short (x10) | RD | Fourier analysis: 21. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 11066 | short (x10) | RD | Fourier analysis: 23. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 11067 | short (x10) | RD | Fourier analysis: 25. harmonic voltage L3 | V
Fourieranalyse, Messwerte | 41 | 11068 | short (x10) | RD | Fourier analysis: 1. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 11069 | short (x10) | RD | Fourier analysis: 3. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 11070 | short (x10) | RD | Fourier analysis: 5. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 11071 | short (x10) | RD | Fourier analysis: 7. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 11072 | short (x10) | RD | Fourier analysis: 9. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 11073 | short (x10) | RD | Fourier analysis: 11. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 11074 | short (x10) | RD | Fourier analysis: 13. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 11075 | short (x10) | RD | Fourier analysis: 15. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 11076 | short (x10) | RD | Fourier analysis: 17. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 11077 | short (x10) | RD | Fourier analysis: 19. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 11078 | short (x10) | RD | Fourier analysis: 21. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 11079 | short (x10) | RD | Fourier analysis: 23. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 11080 | short (x10) | RD | Fourier analysis: 25. harmonic current L1 | A
Fourieranalyse, Messwerte | 41 | 11081 | short (x10) | RD | Fourier analysis: 1. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 11082 | short (x10) | RD | Fourier analysis: 3. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 11083 | short (x10) | RD | Fourier analysis: 5. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 11084 | short (x10) | RD | Fourier analysis: 7. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 11085 | short (x10) | RD | Fourier analysis: 9. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 11086 | short (x10) | RD | Fourier analysis: 11. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 11087 | short (x10) | RD | Fourier analysis: 13. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 11088 | short (x10) | RD | Fourier analysis: 15. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 11089 | short (x10) | RD | Fourier analysis: 17. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 11090 | short (x10) | RD | Fourier analysis: 19. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 11091 | short (x10) | RD | Fourier analysis: 21. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 11092 | short (x10) | RD | Fourier analysis: 23. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 11093 | short (x10) | RD | Fourier analysis: 25. harmonic current L2 | A
Fourieranalyse, Messwerte | 41 | 11094 | short (x10) | RD | Fourier analysis: 1. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 11095 | short (x10) | RD | Fourier analysis: 3. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 11096 | short (x10) | RD | Fourier analysis: 5. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 11097 | short (x10) | RD | Fourier analysis: 7. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 11098 | short (x10) | RD | Fourier analysis: 9. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 11099 | short (x10) | RD | Fourier analysis: 11. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 11100 | short (x10) | RD | Fourier analysis: 13. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 11101 | short (x10) | RD | Fourier analysis: 15. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 11102 | short (x10) | RD | Fourier analysis: 17. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 11103 | short (x10) | RD | Fourier analysis: 19. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 11104 | short (x10) | RD | Fourier analysis: 21. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 11105 | short (x10) | RD | Fourier analysis: 23. harmonic current L3 | A
Fourieranalyse, Messwerte | 41 | 11106 | short (x10) | RD | Fourier analysis: 25. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 3058 | float | RD | Max. value: 1. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 3060 | float | RD | Max. value: 3. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 3062 | float | RD | Max. value: 5. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 3064 | float | RD | Max. value: 7. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 3066 | float | RD | Max. value: 9. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 3068 | float | RD | Max. value: 11. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 3070 | float | RD | Max. value: 13. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 3072 | float | RD | Max. value: 15. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 3074 | float | RD | Max. value: 17. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 3076 | float | RD | Max. value: 19. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 3078 | float | RD | Max. value: 21. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 3080 | float | RD | Max. value: 23. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 3082 | float | RD | Max. value: 25. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 3084 | float | RD | Max. value: 1. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 3086 | float | RD | Max. value: 3. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 3088 | float | RD | Max. value: 5. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 3090 | float | RD | Max. value: 7. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 3092 | float | RD | Max. value: 9. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 3094 | float | RD | Max. value: 11. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 3096 | float | RD | Max. value: 13. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 3098 | float | RD | Max. value: 15. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 3100 | float | RD | Max. value: 17. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 3102 | float | RD | Max. value: 19. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 3104 | float | RD | Max. value: 21. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 3106 | float | RD | Max. value: 23. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 3108 | float | RD | Max. value: 25. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 3110 | float | RD | Max. value: 1. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 3112 | float | RD | Max. value: 3. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 3114 | float | RD | Max. value: 5. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 3116 | float | RD | Max. value: 7. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 3118 | float | RD | Max. value: 9. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 3120 | float | RD | Max. value: 11. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 3122 | float | RD | Max. value: 13. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 3124 | float | RD | Max. value: 15. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 3126 | float | RD | Max. value: 17. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 3128 | float | RD | Max. value: 19. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 3130 | float | RD | Max. value: 21. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 3132 | float | RD | Max. value: 23. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 3134 | float | RD | Max. value: 25. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 3136 | float | RD | Max. value: 1. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 3138 | float | RD | Max. value: 3. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 3140 | float | RD | Max. value: 5. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 3142 | float | RD | Max. value: 7. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 3144 | float | RD | Max. value: 9. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 3146 | float | RD | Max. value: 11. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 3148 | float | RD | Max. value: 13. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 3150 | float | RD | Max. value: 15. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 3152 | float | RD | Max. value: 17. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 3154 | float | RD | Max. value: 19. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 3156 | float | RD | Max. value: 21. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 3158 | float | RD | Max. value: 23. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 3160 | float | RD | Max. value: 25. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 3162 | float | RD | Max. value: 1. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 3164 | float | RD | Max. value: 3. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 3166 | float | RD | Max. value: 5. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 3168 | float | RD | Max. value: 7. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 3170 | float | RD | Max. value: 9. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 3172 | float | RD | Max. value: 11. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 3174 | float | RD | Max. value: 13. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 3176 | float | RD | Max. value: 15. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 3178 | float | RD | Max. value: 17. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 3180 | float | RD | Max. value: 19. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 3182 | float | RD | Max. value: 21. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 3184 | float | RD | Max. value: 23. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 3186 | float | RD | Max. value: 25. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 3188 | float | RD | Max. value: 1. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 3190 | float | RD | Max. value: 3. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 3192 | float | RD | Max. value: 5. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 3194 | float | RD | Max. value: 7. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 3196 | float | RD | Max. value: 9. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 3198 | float | RD | Max. value: 11. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 3200 | float | RD | Max. value: 13. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 3202 | float | RD | Max. value: 15. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 3204 | float | RD | Max. value: 17. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 3206 | float | RD | Max. value: 19. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 3208 | float | RD | Max. value: 21. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 3210 | float | RD | Max. value: 23. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 3212 | float | RD | Max. value: 25. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 8960 | float | RD | Max. value: 1. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 8962 | float | RD | Max. value: 2. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 8964 | float | RD | Max. value: 3. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 8966 | float | RD | Max. value: 4. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 8968 | float | RD | Max. value: 5. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 8970 | float | RD | Max. value: 6. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 8972 | float | RD | Max. value: 7. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 8974 | float | RD | Max. value: 8. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 8976 | float | RD | Max. value: 9. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 8978 | float | RD | Max. value: 10. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 8980 | float | RD | Max. value: 11. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 8982 | float | RD | Max. value: 12. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 8984 | float | RD | Max. value: 13. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 8986 | float | RD | Max. value: 14. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 8988 | float | RD | Max. value: 15. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 8990 | float | RD | Max. value: 16. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 8992 | float | RD | Max. value: 17. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 8994 | float | RD | Max. value: 18. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 8996 | float | RD | Max. value: 19. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 8998 | float | RD | Max. value: 20. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 9000 | float | RD | Max. value: 21. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 9002 | float | RD | Max. value: 22. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 9004 | float | RD | Max. value: 23. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 9006 | float | RD | Max. value: 24. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 9008 | float | RD | Max. value: 25. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 9010 | float | RD | Max. value: 26. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 9012 | float | RD | Max. value: 26. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 9014 | float | RD | Max. value: 28. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 9016 | float | RD | Max. value: 29. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 9018 | float | RD | Max. value: 30. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 9020 | float | RD | Max. value: 31. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 9022 | float | RD | Max. value: 32. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 9024 | float | RD | Max. value: 33. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 9026 | float | RD | Max. value: 34. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 9028 | float | RD | Max. value: 35. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 9030 | float | RD | Max. value: 36. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 9032 | float | RD | Max. value: 37. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 9034 | float | RD | Max. value: 38. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 9036 | float | RD | Max. value: 39. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 9038 | float | RD | Max. value: 40. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 9040 | float | RD | Max. value: 1. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9042 | float | RD | Max. value: 2. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9044 | float | RD | Max. value: 3. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9046 | float | RD | Max. value: 4. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9048 | float | RD | Max. value: 5. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9050 | float | RD | Max. value: 6. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9052 | float | RD | Max. value: 7. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9054 | float | RD | Max. value: 8. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9056 | float | RD | Max. value: 9. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9058 | float | RD | Max. value: 10. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9060 | float | RD | Max. value: 11. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9062 | float | RD | Max. value: 12. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9064 | float | RD | Max. value: 13. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9066 | float | RD | Max. value: 14. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9068 | float | RD | Max. value: 15. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9070 | float | RD | Max. value: 16. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9072 | float | RD | Max. value: 17. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9074 | float | RD | Max. value: 18. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9076 | float | RD | Max. value: 19. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9078 | float | RD | Max. value: 20. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9080 | float | RD | Max. value: 21. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9082 | float | RD | Max. value: 22. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9084 | float | RD | Max. value: 23. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9086 | float | RD | Max. value: 24. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9088 | float | RD | Max. value: 25. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9090 | float | RD | Max. value: 26. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9092 | float | RD | Max. value: 27. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9094 | float | RD | Max. value: 28. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9096 | float | RD | Max. value: 29. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9098 | float | RD | Max. value: 30. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9100 | float | RD | Max. value: 31. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9102 | float | RD | Max. value: 32. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9104 | float | RD | Max. value: 33. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9106 | float | RD | Max. value: 34. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9108 | float | RD | Max. value: 35. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9110 | float | RD | Max. value: 36. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9112 | float | RD | Max. value: 37. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9114 | float | RD | Max. value: 38. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9116 | float | RD | Max. value: 39. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9118 | float | RD | Max. value: 40. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 9120 | float | RD | Max. value: 1. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9122 | float | RD | Max. value: 2. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9124 | float | RD | Max. value: 3. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9126 | float | RD | Max. value: 4. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9128 | float | RD | Max. value: 5. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9130 | float | RD | Max. value: 6. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9132 | float | RD | Max. value: 7. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9134 | float | RD | Max. value: 8. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9136 | float | RD | Max. value: 9. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9138 | float | RD | Max. value: 10. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9140 | float | RD | Max. value: 11. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9142 | float | RD | Max. value: 12. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9144 | float | RD | Max. value: 13. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9146 | float | RD | Max. value: 14. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9148 | float | RD | Max. value: 15. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9150 | float | RD | Max. value: 16. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9152 | float | RD | Max. value: 17. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9154 | float | RD | Max. value: 18. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9156 | float | RD | Max. value: 19. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9158 | float | RD | Max. value: 20. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9160 | float | RD | Max. value: 21. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9162 | float | RD | Max. value: 22. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9164 | float | RD | Max. value: 23. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9166 | float | RD | Max. value: 24. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9168 | float | RD | Max. value: 25. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9170 | float | RD | Max. value: 26. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9172 | float | RD | Max. value: 27. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9174 | float | RD | Max. value: 28. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9176 | float | RD | Max. value: 29. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9178 | float | RD | Max. value: 30. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9180 | float | RD | Max. value: 31. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9182 | float | RD | Max. value: 32. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9184 | float | RD | Max. value: 33. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9186 | float | RD | Max. value: 34. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9188 | float | RD | Max. value: 35. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9190 | float | RD | Max. value: 36. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9192 | float | RD | Max. value: 37. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9194 | float | RD | Max. value: 38. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9196 | float | RD | Max. value: 39. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9198 | float | RD | Max. value: 40. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 9200 | float | RD | Max. value: 1. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9202 | float | RD | Max. value: 2. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9204 | float | RD | Max. value: 3. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9206 | float | RD | Max. value: 4. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9208 | float | RD | Max. value: 5. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9210 | float | RD | Max. value: 6. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9212 | float | RD | Max. value: 7. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9214 | float | RD | Max. value: 8. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9216 | float | RD | Max. value: 9. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9218 | float | RD | Max. value: 10. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9220 | float | RD | Max. value: 11. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9222 | float | RD | Max. value: 12. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9224 | float | RD | Max. value: 13. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9226 | float | RD | Max. value: 14. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9228 | float | RD | Max. value: 15. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9230 | float | RD | Max. value: 16. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9232 | float | RD | Max. value: 17. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9234 | float | RD | Max. value: 18. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9236 | float | RD | Max. value: 19. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9238 | float | RD | Max. value: 20. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9240 | float | RD | Max. value: 21. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9242 | float | RD | Max. value: 22. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9244 | float | RD | Max. value: 23. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9246 | float | RD | Max. value: 24. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9248 | float | RD | Max. value: 25. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9250 | float | RD | Max. value: 26. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9252 | float | RD | Max. value: 27. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9254 | float | RD | Max. value: 28. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9256 | float | RD | Max. value: 29. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9258 | float | RD | Max. value: 30. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9260 | float | RD | Max. value: 31. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9262 | float | RD | Max. value: 32. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9264 | float | RD | Max. value: 33. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9266 | float | RD | Max. value: 34. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9268 | float | RD | Max. value: 35. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9270 | float | RD | Max. value: 36. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9272 | float | RD | Max. value: 37. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9274 | float | RD | Max. value: 38. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9276 | float | RD | Max. value: 39. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9278 | float | RD | Max. value: 40. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 9280 | float | RD | Max. value: 1. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9282 | float | RD | Max. value: 2. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9284 | float | RD | Max. value: 3. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9286 | float | RD | Max. value: 4. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9288 | float | RD | Max. value: 5. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9290 | float | RD | Max. value: 6. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9292 | float | RD | Max. value: 7. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9294 | float | RD | Max. value: 8. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9296 | float | RD | Max. value: 9. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9298 | float | RD | Max. value: 10. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9300 | float | RD | Max. value: 11. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9302 | float | RD | Max. value: 12. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9304 | float | RD | Max. value: 13. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9306 | float | RD | Max. value: 14. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9308 | float | RD | Max. value: 15. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9310 | float | RD | Max. value: 16. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9312 | float | RD | Max. value: 17. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9314 | float | RD | Max. value: 18. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9316 | float | RD | Max. value: 19. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9318 | float | RD | Max. value: 20. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9320 | float | RD | Max. value: 21. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9322 | float | RD | Max. value: 22. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9324 | float | RD | Max. value: 23. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9326 | float | RD | Max. value: 24. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9328 | float | RD | Max. value: 25. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9330 | float | RD | Max. value: 26. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9332 | float | RD | Max. value: 27. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9334 | float | RD | Max. value: 28. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9336 | float | RD | Max. value: 29. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9338 | float | RD | Max. value: 30. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9340 | float | RD | Max. value: 31. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9342 | float | RD | Max. value: 32. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9344 | float | RD | Max. value: 33. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9346 | float | RD | Max. value: 34. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9348 | float | RD | Max. value: 35. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9350 | float | RD | Max. value: 36. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9352 | float | RD | Max. value: 37. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9354 | float | RD | Max. value: 38. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9356 | float | RD | Max. value: 39. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9358 | float | RD | Max. value: 40. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 9360 | float | RD | Max. value: 1. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9362 | float | RD | Max. value: 2. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9364 | float | RD | Max. value: 3. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9366 | float | RD | Max. value: 4. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9368 | float | RD | Max. value: 5. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9370 | float | RD | Max. value: 6. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9372 | float | RD | Max. value: 7. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9374 | float | RD | Max. value: 8. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9376 | float | RD | Max. value: 9. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9378 | float | RD | Max. value: 10. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9380 | float | RD | Max. value: 11. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9382 | float | RD | Max. value: 12. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9384 | float | RD | Max. value: 13. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9386 | float | RD | Max. value: 14. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9388 | float | RD | Max. value: 15. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9390 | float | RD | Max. value: 16. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9392 | float | RD | Max. value: 17. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9394 | float | RD | Max. value: 18. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9396 | float | RD | Max. value: 19. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9398 | float | RD | Max. value: 20. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9400 | float | RD | Max. value: 21. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9402 | float | RD | Max. value: 22. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9404 | float | RD | Max. value: 23. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9406 | float | RD | Max. value: 24. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9408 | float | RD | Max. value: 25. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9410 | float | RD | Max. value: 26. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9412 | float | RD | Max. value: 27. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9414 | float | RD | Max. value: 28. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9416 | float | RD | Max. value: 29. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9418 | float | RD | Max. value: 30. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9420 | float | RD | Max. value: 31. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9422 | float | RD | Max. value: 32. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9424 | float | RD | Max. value: 33. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9426 | float | RD | Max. value: 34. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9428 | float | RD | Max. value: 35. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9430 | float | RD | Max. value: 36. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9432 | float | RD | Max. value: 37. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9434 | float | RD | Max. value: 38. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9436 | float | RD | Max. value: 39. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 9438 | float | RD | Max. value: 40. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 13029 | short (x10) | RD | Max. value: 1. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 13030 | short (x10) | RD | Max. value: 3. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 13031 | short (x10) | RD | Max. value: 5. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 13032 | short (x10) | RD | Max. value: 7. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 13033 | short (x10) | RD | Max. value: 9. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 13034 | short (x10) | RD | Max. value: 11. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 13035 | short (x10) | RD | Max. value: 13. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 13036 | short (x10) | RD | Max. value: 15. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 13037 | short (x10) | RD | Max. value: 17. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 13038 | short (x10) | RD | Max. value: 19. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 13039 | short (x10) | RD | Max. value: 21. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 13040 | short (x10) | RD | Max. value: 23. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 13041 | short (x10) | RD | Max. value: 25. harmonic voltage L1 | V
Maximalwerte, Fourieranalyse | 43 | 13042 | short (x10) | RD | Max. value: 1. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 13043 | short (x10) | RD | Max. value: 3. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 13044 | short (x10) | RD | Max. value: 5. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 13045 | short (x10) | RD | Max. value: 7. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 13046 | short (x10) | RD | Max. value: 9. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 13047 | short (x10) | RD | Max. value: 11. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 13048 | short (x10) | RD | Max. value: 13. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 13049 | short (x10) | RD | Max. value: 15. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 13050 | short (x10) | RD | Max. value: 17. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 13051 | short (x10) | RD | Max. value: 19. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 13052 | short (x10) | RD | Max. value: 21. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 13053 | short (x10) | RD | Max. value: 23. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 13054 | short (x10) | RD | Max. value: 25. harmonic voltage L2 | V
Maximalwerte, Fourieranalyse | 43 | 13055 | short (x10) | RD | Max. value: 1. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 13056 | short (x10) | RD | Max. value: 3. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 13057 | short (x10) | RD | Max. value: 5. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 13058 | short (x10) | RD | Max. value: 7. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 13059 | short (x10) | RD | Max. value: 9. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 13060 | short (x10) | RD | Max. value: 11. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 13061 | short (x10) | RD | Max. value: 13. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 13062 | short (x10) | RD | Max. value: 15. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 13063 | short (x10) | RD | Max. value: 17. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 13064 | short (x10) | RD | Max. value: 19. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 13065 | short (x10) | RD | Max. value: 21. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 13066 | short (x10) | RD | Max. value: 23. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 13067 | short (x10) | RD | Max. value: 25. harmonic voltage L3 | V
Maximalwerte, Fourieranalyse | 43 | 13068 | short (x1000) | RD | Max. value: 1. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 13069 | short (x1000) | RD | Max. value: 3. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 13070 | short (x1000) | RD | Max. value: 5. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 13071 | short (x1000) | RD | Max. value: 7. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 13072 | short (x1000) | RD | Max. value: 9. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 13073 | short (x1000) | RD | Max. value: 11. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 13074 | short (x1000) | RD | Max. value: 13. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 13075 | short (x1000) | RD | Max. value: 15. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 13076 | short (x1000) | RD | Max. value: 17. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 13077 | short (x1000) | RD | Max. value: 19. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 13078 | short (x1000) | RD | Max. value: 21. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 13079 | short (x1000) | RD | Max. value: 23. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 13080 | short (x1000) | RD | Max. value: 25. harmonic current L1 | A
Maximalwerte, Fourieranalyse | 43 | 13081 | short (x1000) | RD | Max. value: 1. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 13082 | short (x1000) | RD | Max. value: 3. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 13083 | short (x1000) | RD | Max. value: 5. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 13084 | short (x1000) | RD | Max. value: 7. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 13085 | short (x1000) | RD | Max. value: 9. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 13086 | short (x1000) | RD | Max. value: 11. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 13087 | short (x1000) | RD | Max. value: 13. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 13088 | short (x1000) | RD | Max. value: 15. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 13089 | short (x1000) | RD | Max. value: 17. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 13090 | short (x1000) | RD | Max. value: 19. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 13091 | short (x1000) | RD | Max. value: 21. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 13092 | short (x1000) | RD | Max. value: 23. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 13093 | short (x1000) | RD | Max. value: 25. harmonic current L2 | A
Maximalwerte, Fourieranalyse | 43 | 13094 | short (x1000) | RD | Max. value: 1. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 13095 | short (x1000) | RD | Max. value: 3. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 13096 | short (x1000) | RD | Max. value: 5. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 13097 | short (x1000) | RD | Max. value: 7. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 13098 | short (x1000) | RD | Max. value: 9. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 13099 | short (x1000) | RD | Max. value: 11. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 13100 | short (x1000) | RD | Max. value: 13. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 13101 | short (x1000) | RD | Max. value: 15. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 13102 | short (x1000) | RD | Max. value: 17. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 13103 | short (x1000) | RD | Max. value: 17. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 13104 | short (x1000) | RD | Max. value: 21. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 13105 | short (x1000) | RD | Max. value: 23. harmonic current L3 | A
Maximalwerte, Fourieranalyse | 43 | 13106 | short (x1000) | RD | Max. value: 25. harmonic current L3 | A
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3358 | uint | RD | UTC timestamp, max. value: 1. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3360 | uint | RD | UTC timestamp, max. value: 3. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3362 | uint | RD | UTC timestamp, max. value: 5. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3364 | uint | RD | UTC timestamp, max. value: 7. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3366 | uint | RD | UTC timestamp, max. value: 9. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3368 | uint | RD | UTC timestamp, max. value: 11. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3370 | uint | RD | UTC timestamp, max. value: 13. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3372 | uint | RD | UTC timestamp, max. value: 15. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3374 | uint | RD | UTC timestamp, max. value: 17. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3376 | uint | RD | UTC timestamp, max. value: 19. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3378 | uint | RD | UTC timestamp, max. value: 21. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3380 | uint | RD | UTC timestamp, max. value: 23. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3382 | uint | RD | UTC timestamp, max. value: 25. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3384 | uint | RD | UTC timestamp, max. value: 1. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3386 | uint | RD | UTC timestamp, max. value: 3. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3388 | uint | RD | UTC timestamp, max. value: 5. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3390 | uint | RD | UTC timestamp, max. value: 7. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3392 | uint | RD | UTC timestamp, max. value: 9. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3394 | uint | RD | UTC timestamp, max. value: 11. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3396 | uint | RD | UTC timestamp, max. value: 13. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3398 | uint | RD | UTC timestamp, max. value: 15. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3400 | uint | RD | UTC timestamp, max. value: 17. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3402 | uint | RD | UTC timestamp, max. value: 19. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3404 | uint | RD | UTC timestamp, max. value: 21. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3406 | uint | RD | UTC timestamp, max. value: 23. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3408 | uint | RD | UTC timestamp, max. value: 25. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3410 | uint | RD | UTC timestamp, max. value: 1. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3412 | uint | RD | UTC timestamp, max. value: 3. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3414 | uint | RD | UTC timestamp, max. value: 5. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3416 | uint | RD | UTC timestamp, max. value: 7. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3418 | uint | RD | UTC timestamp, max. value: 9. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3420 | uint | RD | UTC timestamp, max. value: 11. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3422 | uint | RD | UTC timestamp, max. value: 13. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3424 | uint | RD | UTC timestamp, max. value: 15. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3426 | uint | RD | UTC timestamp, max. value: 17. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3428 | uint | RD | UTC timestamp, max. value: 19. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3430 | uint | RD | UTC timestamp, max. value: 21. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3432 | uint | RD | UTC timestamp, max. value: 23. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3434 | uint | RD | UTC timestamp, max. value: 25. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3436 | uint | RD | UTC timestamp, max. value: 1. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3438 | uint | RD | UTC timestamp, max. value: 3. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3440 | uint | RD | UTC timestamp, max. value: 5. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3442 | uint | RD | UTC timestamp, max. value: 7. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3444 | uint | RD | UTC timestamp, max. value: 9. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3446 | uint | RD | UTC timestamp, max. value: 11. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3448 | uint | RD | UTC timestamp, max. value: 13. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3450 | uint | RD | UTC timestamp, max. value: 15. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3452 | uint | RD | UTC timestamp, max. value: 17. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3454 | uint | RD | UTC timestamp, max. value: 19. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3456 | uint | RD | UTC timestamp, max. value: 21. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3458 | uint | RD | UTC timestamp, max. value: 23. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3460 | uint | RD | UTC timestamp, max. value: 25. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3462 | uint | RD | UTC timestamp, max. value: 1. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3464 | uint | RD | UTC timestamp, max. value: 3. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3466 | uint | RD | UTC timestamp, max. value: 5. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3468 | uint | RD | UTC timestamp, max. value: 7. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3470 | uint | RD | UTC timestamp, max. value: 9. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3472 | uint | RD | UTC timestamp, max. value: 11. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3474 | uint | RD | UTC timestamp, max. value: 13. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3476 | uint | RD | UTC timestamp, max. value: 15. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3478 | uint | RD | UTC timestamp, max. value: 17. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3480 | uint | RD | UTC timestamp, max. value: 19. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3482 | uint | RD | UTC timestamp, max. value: 21. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3484 | uint | RD | UTC timestamp, max. value: 23. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3486 | uint | RD | UTC timestamp, max. value: 25. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3488 | uint | RD | UTC timestamp, max. value: 1. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3490 | uint | RD | UTC timestamp, max. value: 3. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3492 | uint | RD | UTC timestamp, max. value: 5. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3494 | uint | RD | UTC timestamp, max. value: 7. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3496 | uint | RD | UTC timestamp, max. value: 9. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3498 | uint | RD | UTC timestamp, max. value: 11. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3500 | uint | RD | UTC timestamp, max. value: 13. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3502 | uint | RD | UTC timestamp, max. value: 15. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3504 | uint | RD | UTC timestamp, max. value: 17. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3506 | uint | RD | UTC timestamp, max. value: 19. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3508 | uint | RD | UTC timestamp, max. value: 21. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3510 | uint | RD | UTC timestamp, max. value: 23. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 3512 | uint | RD | UTC timestamp, max. value: 25. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9440 | uint | RD | UTC timestamp, max. value: 1. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9442 | uint | RD | UTC timestamp, max. value: 2. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9444 | uint | RD | UTC timestamp, max. value: 3. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9446 | uint | RD | UTC timestamp, max. value: 4. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9448 | uint | RD | UTC timestamp, max. value: 5. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9450 | uint | RD | UTC timestamp, max. value: 6. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9452 | uint | RD | UTC timestamp, max. value: 7. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9454 | uint | RD | UTC timestamp, max. value: 8. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9456 | uint | RD | UTC timestamp, max. value: 9. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9458 | uint | RD | UTC timestamp, max. value: 10. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9460 | uint | RD | UTC timestamp, max. value: 11. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9462 | uint | RD | UTC timestamp, max. value: 12. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9464 | uint | RD | UTC timestamp, max. value: 13. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9466 | uint | RD | UTC timestamp, max. value: 14. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9468 | uint | RD | UTC timestamp, max. value: 15. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9470 | uint | RD | UTC timestamp, max. value: 16. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9472 | uint | RD | UTC timestamp, max. value: 17. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9474 | uint | RD | UTC timestamp, max. value: 18. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9476 | uint | RD | UTC timestamp, max. value: 19. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9478 | uint | RD | UTC timestamp, max. value: 20. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9480 | uint | RD | UTC timestamp, max. value: 21. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9482 | uint | RD | UTC timestamp, max. value: 22. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9484 | uint | RD | UTC timestamp, max. value: 23. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9486 | uint | RD | UTC timestamp, max. value: 24. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9488 | uint | RD | UTC timestamp, max. value: 25. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9490 | uint | RD | UTC timestamp, max. value: 26. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9492 | uint | RD | UTC timestamp, max. value: 27. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9494 | uint | RD | UTC timestamp, max. value: 28. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9496 | uint | RD | UTC timestamp, max. value: 29. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9498 | uint | RD | UTC timestamp, max. value: 30. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9500 | uint | RD | UTC timestamp, max. value: 31. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9502 | uint | RD | UTC timestamp, max. value: 32. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9504 | uint | RD | UTC timestamp, max. value: 33. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9506 | uint | RD | UTC timestamp, max. value: 34. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9508 | uint | RD | UTC timestamp, max. value: 35. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9510 | uint | RD | UTC timestamp, max. value: 36. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9512 | uint | RD | UTC timestamp, max. value: 37. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9514 | uint | RD | UTC timestamp, max. value: 38. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9516 | uint | RD | UTC timestamp, max. value: 39. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9518 | uint | RD | UTC timestamp, max. value: 40. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9520 | uint | RD | UTC timestamp, max. value: 1. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9522 | uint | RD | UTC timestamp, max. value: 2. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9524 | uint | RD | UTC timestamp, max. value: 3. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9526 | uint | RD | UTC timestamp, max. value: 4. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9528 | uint | RD | UTC timestamp, max. value: 5. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9530 | uint | RD | UTC timestamp, max. value: 6. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9532 | uint | RD | UTC timestamp, max. value: 7. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9534 | uint | RD | UTC timestamp, max. value: 8. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9536 | uint | RD | UTC timestamp, max. value: 9. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9538 | uint | RD | UTC timestamp, max. value: 10. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9540 | uint | RD | UTC timestamp, max. value: 11. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9542 | uint | RD | UTC timestamp, max. value: 12. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9544 | uint | RD | UTC timestamp, max. value: 13. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9546 | uint | RD | UTC timestamp, max. value: 14. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9548 | uint | RD | UTC timestamp, max. value: 15. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9550 | uint | RD | UTC timestamp, max. value: 16. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9552 | uint | RD | UTC timestamp, max. value: 17. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9554 | uint | RD | UTC timestamp, max. value: 18. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9556 | uint | RD | UTC timestamp, max. value: 19. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9558 | uint | RD | UTC timestamp, max. value: 20. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9560 | uint | RD | UTC timestamp, max. value: 21. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9562 | uint | RD | UTC timestamp, max. value: 22. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9564 | uint | RD | UTC timestamp, max. value: 23. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9566 | uint | RD | UTC timestamp, max. value: 24. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9568 | uint | RD | UTC timestamp, max. value: 25. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9570 | uint | RD | UTC timestamp, max. value: 26. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9572 | uint | RD | UTC timestamp, max. value: 27. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9574 | uint | RD | UTC timestamp, max. value: 28. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9576 | uint | RD | UTC timestamp, max. value: 29. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9578 | uint | RD | UTC timestamp, max. value: 30. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9580 | uint | RD | UTC timestamp, max. value: 31. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9582 | uint | RD | UTC timestamp, max. value: 32. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9584 | uint | RD | UTC timestamp, max. value: 33. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9586 | uint | RD | UTC timestamp, max. value: 34. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9588 | uint | RD | UTC timestamp, max. value: 35. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9590 | uint | RD | UTC timestamp, max. value: 36. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9592 | uint | RD | UTC timestamp, max. value: 37. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9594 | uint | RD | UTC timestamp, max. value: 38. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9596 | uint | RD | UTC timestamp, max. value: 39. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9598 | uint | RD | UTC timestamp, max. value: 40. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9600 | uint | RD | UTC timestamp, max. value: 1. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9602 | uint | RD | UTC timestamp, max. value: 2. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9604 | uint | RD | UTC timestamp, max. value: 3. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9606 | uint | RD | UTC timestamp, max. value: 4. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9608 | uint | RD | UTC timestamp, max. value: 5. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9610 | uint | RD | UTC timestamp, max. value: 6. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9612 | uint | RD | UTC timestamp, max. value: 7. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9614 | uint | RD | UTC timestamp, max. value: 8. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9616 | uint | RD | UTC timestamp, max. value: 9. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9618 | uint | RD | UTC timestamp, max. value: 10. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9620 | uint | RD | UTC timestamp, max. value: 11. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9622 | uint | RD | UTC timestamp, max. value: 12. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9624 | uint | RD | UTC timestamp, max. value: 13. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9626 | uint | RD | UTC timestamp, max. value: 14. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9628 | uint | RD | UTC timestamp, max. value: 15. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9630 | uint | RD | UTC timestamp, max. value: 16. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9632 | uint | RD | UTC timestamp, max. value: 17. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9634 | uint | RD | UTC timestamp, max. value: 18. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9636 | uint | RD | UTC timestamp, max. value: 19. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9638 | uint | RD | UTC timestamp, max. value: 20. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9640 | uint | RD | UTC timestamp, max. value: 21. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9642 | uint | RD | UTC timestamp, max. value: 22. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9644 | uint | RD | UTC timestamp, max. value: 23. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9646 | uint | RD | UTC timestamp, max. value: 24. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9648 | uint | RD | UTC timestamp, max. value: 25. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9650 | uint | RD | UTC timestamp, max. value: 26. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9652 | uint | RD | UTC timestamp, max. value: 27. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9654 | uint | RD | UTC timestamp, max. value: 28. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9656 | uint | RD | UTC timestamp, max. value: 29. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9658 | uint | RD | UTC timestamp, max. value: 30. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9660 | uint | RD | UTC timestamp, max. value: 31. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9662 | uint | RD | UTC timestamp, max. value: 32. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9664 | uint | RD | UTC timestamp, max. value: 33. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9666 | uint | RD | UTC timestamp, max. value: 34. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9668 | uint | RD | UTC timestamp, max. value: 35. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9670 | uint | RD | UTC timestamp, max. value: 36. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9672 | uint | RD | UTC timestamp, max. value: 37. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9674 | uint | RD | UTC timestamp, max. value: 38. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9676 | uint | RD | UTC timestamp, max. value: 39. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9678 | uint | RD | UTC timestamp, max. value: 40. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9680 | uint | RD | UTC timestamp, max. value: 1. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9682 | uint | RD | UTC timestamp, max. value: 2. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9684 | uint | RD | UTC timestamp, max. value: 3. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9686 | uint | RD | UTC timestamp, max. value: 4. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9688 | uint | RD | UTC timestamp, max. value: 5. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9690 | uint | RD | UTC timestamp, max. value: 6. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9692 | uint | RD | UTC timestamp, max. value: 7. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9694 | uint | RD | UTC timestamp, max. value: 8. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9696 | uint | RD | UTC timestamp, max. value: 9. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9698 | uint | RD | UTC timestamp, max. value: 10. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9700 | uint | RD | UTC timestamp, max. value: 11. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9702 | uint | RD | UTC timestamp, max. value: 12. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9704 | uint | RD | UTC timestamp, max. value: 13. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9706 | uint | RD | UTC timestamp, max. value: 14. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9708 | uint | RD | UTC timestamp, max. value: 15. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9710 | uint | RD | UTC timestamp, max. value: 16. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9712 | uint | RD | UTC timestamp, max. value: 17. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9714 | uint | RD | UTC timestamp, max. value: 18. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9716 | uint | RD | UTC timestamp, max. value: 19. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9718 | uint | RD | UTC timestamp, max. value: 20. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9720 | uint | RD | UTC timestamp, max. value: 21. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9722 | uint | RD | UTC timestamp, max. value: 22. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9724 | uint | RD | UTC timestamp, max. value: 23. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9726 | uint | RD | UTC timestamp, max. value: 24. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9728 | uint | RD | UTC timestamp, max. value: 25. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9730 | uint | RD | UTC timestamp, max. value: 26. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9732 | uint | RD | UTC timestamp, max. value: 27. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9734 | uint | RD | UTC timestamp, max. value: 28. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9736 | uint | RD | UTC timestamp, max. value: 29. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9738 | uint | RD | UTC timestamp, max. value: 30. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9740 | uint | RD | UTC timestamp, max. value: 31. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9742 | uint | RD | UTC timestamp, max. value: 32. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9744 | uint | RD | UTC timestamp, max. value: 33. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9746 | uint | RD | UTC timestamp, max. value: 34. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9748 | uint | RD | UTC timestamp, max. value: 35. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9750 | uint | RD | UTC timestamp, max. value: 36. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9752 | uint | RD | UTC timestamp, max. value: 37. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9754 | uint | RD | UTC timestamp, max. value: 38. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9756 | uint | RD | UTC timestamp, max. value: 39. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9758 | uint | RD | UTC timestamp, max. value: 40. harmonic current L1 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9760 | uint | RD | UTC timestamp, max. value: 1. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9762 | uint | RD | UTC timestamp, max. value: 2. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9764 | uint | RD | UTC timestamp, max. value: 3. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9766 | uint | RD | UTC timestamp, max. value: 4. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9768 | uint | RD | UTC timestamp, max. value: 5. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9770 | uint | RD | UTC timestamp, max. value: 6. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9772 | uint | RD | UTC timestamp, max. value: 7. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9774 | uint | RD | UTC timestamp, max. value: 8. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9776 | uint | RD | UTC timestamp, max. value: 9. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9778 | uint | RD | UTC timestamp, max. value: 10. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9780 | uint | RD | UTC timestamp, max. value: 11. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9782 | uint | RD | UTC timestamp, max. value: 12. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9784 | uint | RD | UTC timestamp, max. value: 13. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9786 | uint | RD | UTC timestamp, max. value: 14. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9788 | uint | RD | UTC timestamp, max. value: 15. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9790 | uint | RD | UTC timestamp, max. value: 16. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9792 | uint | RD | UTC timestamp, max. value: 17. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9794 | uint | RD | UTC timestamp, max. value: 18. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9796 | uint | RD | UTC timestamp, max. value: 19. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9798 | uint | RD | UTC timestamp, max. value: 20. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9800 | uint | RD | UTC timestamp, max. value: 21. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9802 | uint | RD | UTC timestamp, max. value: 22. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9804 | uint | RD | UTC timestamp, max. value: 23. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9806 | uint | RD | UTC timestamp, max. value: 24. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9808 | uint | RD | UTC timestamp, max. value: 25. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9810 | uint | RD | UTC timestamp, max. value: 26. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9812 | uint | RD | UTC timestamp, max. value: 27. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9814 | uint | RD | UTC timestamp, max. value: 28. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9816 | uint | RD | UTC timestamp, max. value: 29. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9818 | uint | RD | UTC timestamp, max. value: 30. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9820 | uint | RD | UTC timestamp, max. value: 31. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9822 | uint | RD | UTC timestamp, max. value: 32. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9824 | uint | RD | UTC timestamp, max. value: 33. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9826 | uint | RD | UTC timestamp, max. value: 34. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9828 | uint | RD | UTC timestamp, max. value: 35. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9830 | uint | RD | UTC timestamp, max. value: 36. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9832 | uint | RD | UTC timestamp, max. value: 37. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9834 | uint | RD | UTC timestamp, max. value: 38. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9836 | uint | RD | UTC timestamp, max. value: 39. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9838 | uint | RD | UTC timestamp, max. value: 40. harmonic current L2 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9840 | uint | RD | UTC timestamp, max. value: 1. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9842 | uint | RD | UTC timestamp, max. value: 2. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9844 | uint | RD | UTC timestamp, max. value: 3. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9846 | uint | RD | UTC timestamp, max. value: 4. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9848 | uint | RD | UTC timestamp, max. value: 5. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9850 | uint | RD | UTC timestamp, max. value: 6. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9852 | uint | RD | UTC timestamp, max. value: 7. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9854 | uint | RD | UTC timestamp, max. value: 8. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9856 | uint | RD | UTC timestamp, max. value: 9. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9858 | uint | RD | UTC timestamp, max. value: 10. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9860 | uint | RD | UTC timestamp, max. value: 11. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9862 | uint | RD | UTC timestamp, max. value: 12. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9864 | uint | RD | UTC timestamp, max. value: 13. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9866 | uint | RD | UTC timestamp, max. value: 14. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9868 | uint | RD | UTC timestamp, max. value: 15. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9870 | uint | RD | UTC timestamp, max. value: 16. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9872 | uint | RD | UTC timestamp, max. value: 17. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9874 | uint | RD | UTC timestamp, max. value: 18. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9876 | uint | RD | UTC timestamp, max. value: 19. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9878 | uint | RD | UTC timestamp, max. value: 20. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9880 | uint | RD | UTC timestamp, max. value: 21. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9882 | uint | RD | UTC timestamp, max. value: 22. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9884 | uint | RD | UTC timestamp, max. value: 23. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9886 | uint | RD | UTC timestamp, max. value: 24. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9888 | uint | RD | UTC timestamp, max. value: 25. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9890 | uint | RD | UTC timestamp, max. value: 26. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9892 | uint | RD | UTC timestamp, max. value: 27. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9894 | uint | RD | UTC timestamp, max. value: 28. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9896 | uint | RD | UTC timestamp, max. value: 29. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9898 | uint | RD | UTC timestamp, max. value: 30. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9900 | uint | RD | UTC timestamp, max. value: 31. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9902 | uint | RD | UTC timestamp, max. value: 32. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9904 | uint | RD | UTC timestamp, max. value: 33. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9906 | uint | RD | UTC timestamp, max. value: 34. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9908 | uint | RD | UTC timestamp, max. value: 35. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9910 | uint | RD | UTC timestamp, max. value: 36. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9912 | uint | RD | UTC timestamp, max. value: 37. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9914 | uint | RD | UTC timestamp, max. value: 38. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9916 | uint | RD | UTC timestamp, max. value: 39. harmonic current L3 | s
Maximalwerte, Zeitstempel, Fourieranalyse | 45 | 9918 | uint | RD | UTC timestamp, max. value: 40. harmonic current L3 | s
Minimalwerte, Fourieranalyse | 46 | 4020 | float | RD | Min. value: 1. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 4022 | float | RD | Min. value: 3. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 4024 | float | RD | Min. value: 5. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 4026 | float | RD | Min. value: 7. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 4028 | float | RD | Min. value: 9. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 4030 | float | RD | Min. value: 11. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 4032 | float | RD | Min. value: 13. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 4034 | float | RD | Min. value: 15. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 4036 | float | RD | Min. value: 17. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 4038 | float | RD | Min. value: 19. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 4040 | float | RD | Min. value: 21. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 4042 | float | RD | Min. value: 23. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 4044 | float | RD | Min. value: 25. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 4046 | float | RD | Min. value: 1. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 4048 | float | RD | Min. value: 3. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 4050 | float | RD | Min. value: 5. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 4052 | float | RD | Min. value: 7. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 4054 | float | RD | Min. value: 9. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 4056 | float | RD | Min. value: 11. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 4058 | float | RD | Min. value: 13. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 4060 | float | RD | Min. value: 15. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 4062 | float | RD | Min. value: 17. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 4064 | float | RD | Min. value: 19. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 4066 | float | RD | Min. value: 21. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 4068 | float | RD | Min. value: 23. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 4070 | float | RD | Min. value: 25. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 4072 | float | RD | Min. value: 1. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 4074 | float | RD | Min. value: 3. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 4076 | float | RD | Min. value: 5. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 4078 | float | RD | Min. value: 7. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 4080 | float | RD | Min. value: 9. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 4082 | float | RD | Min. value: 11. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 4084 | float | RD | Min. value: 13. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 4086 | float | RD | Min. value: 15. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 4088 | float | RD | Min. value: 17. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 4090 | float | RD | Min. value: 19. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 4092 | float | RD | Min. value: 21. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 4094 | float | RD | Min. value: 23. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 4096 | float | RD | Min. value: 25. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 9920 | float | RD | Min. value: 1. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9922 | float | RD | Min. value: 2. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9924 | float | RD | Min. value: 3. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9926 | float | RD | Min. value: 4. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9928 | float | RD | Min. value: 5. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9930 | float | RD | Min. value: 6. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9932 | float | RD | Min. value: 7. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9934 | float | RD | Min. value: 8. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9936 | float | RD | Min. value: 9. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9938 | float | RD | Min. value: 10. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9940 | float | RD | Min. value: 11. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9942 | float | RD | Min. value: 12. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9944 | float | RD | Min. value: 13. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9946 | float | RD | Min. value: 14. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9948 | float | RD | Min. value: 15. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9950 | float | RD | Min. value: 16. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9952 | float | RD | Min. value: 17. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9954 | float | RD | Min. value: 18. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9956 | float | RD | Min. value: 19. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9958 | float | RD | Min. value: 20. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9960 | float | RD | Min. value: 21. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9962 | float | RD | Min. value: 22. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9964 | float | RD | Min. value: 23. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9966 | float | RD | Min. value: 24. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9968 | float | RD | Min. value: 25. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9970 | float | RD | Min. value: 26. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9972 | float | RD | Min. value: 27. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9974 | float | RD | Min. value: 28. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9976 | float | RD | Min. value: 29. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9978 | float | RD | Min. value: 30. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9980 | float | RD | Min. value: 31. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9982 | float | RD | Min. value: 32. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9984 | float | RD | Min. value: 33. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9986 | float | RD | Min. value: 34. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9988 | float | RD | Min. value: 35. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9990 | float | RD | Min. value: 36. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9992 | float | RD | Min. value: 37. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9994 | float | RD | Min. value: 38. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9996 | float | RD | Min. value: 39. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 9998 | float | RD | Min. value: 40. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 10000 | float | RD | Min. value: 1. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10002 | float | RD | Min. value: 2. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10004 | float | RD | Min. value: 3. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10006 | float | RD | Min. value: 4. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10008 | float | RD | Min. value: 5. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10010 | float | RD | Min. value: 6. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10012 | float | RD | Min. value: 7. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10014 | float | RD | Min. value: 8. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10016 | float | RD | Min. value: 9. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10018 | float | RD | Min. value: 10. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10020 | float | RD | Min. value: 11. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10022 | float | RD | Min. value: 12. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10024 | float | RD | Min. value: 13. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10026 | float | RD | Min. value: 14. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10028 | float | RD | Min. value: 15. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10030 | float | RD | Min. value: 16. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10032 | float | RD | Min. value: 17. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10034 | float | RD | Min. value: 18. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10036 | float | RD | Min. value: 19. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10038 | float | RD | Min. value: 20. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10040 | float | RD | Min. value: 21. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10042 | float | RD | Min. value: 22. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10044 | float | RD | Min. value: 23. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10046 | float | RD | Min. value: 24. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10048 | float | RD | Min. value: 25. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10050 | float | RD | Min. value: 26. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10052 | float | RD | Min. value: 27. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10054 | float | RD | Min. value: 28. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10056 | float | RD | Min. value: 29. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10058 | float | RD | Min. value: 30. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10060 | float | RD | Min. value: 31. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10062 | float | RD | Min. value: 32. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10064 | float | RD | Min. value: 33. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10066 | float | RD | Min. value: 34. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10068 | float | RD | Min. value: 35. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10070 | float | RD | Min. value: 36. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10072 | float | RD | Min. value: 37. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10074 | float | RD | Min. value: 38. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10076 | float | RD | Min. value: 39. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10078 | float | RD | Min. value: 40. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 10080 | float | RD | Min. value: 1. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10082 | float | RD | Min. value: 2. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10084 | float | RD | Min. value: 3. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10086 | float | RD | Min. value: 4. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10088 | float | RD | Min. value: 5. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10090 | float | RD | Min. value: 6. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10092 | float | RD | Min. value: 7. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10094 | float | RD | Min. value: 8. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10096 | float | RD | Min. value: 9. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10098 | float | RD | Min. value: 10. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10100 | float | RD | Min. value: 11. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10102 | float | RD | Min. value: 12. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10104 | float | RD | Min. value: 13. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10106 | float | RD | Min. value: 14. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10108 | float | RD | Min. value: 15. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10110 | float | RD | Min. value: 16. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10112 | float | RD | Min. value: 17. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10114 | float | RD | Min. value: 18. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10116 | float | RD | Min. value: 19. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10118 | float | RD | Min. value: 20. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10120 | float | RD | Min. value: 21. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10122 | float | RD | Min. value: 22. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10124 | float | RD | Min. value: 23. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10126 | float | RD | Min. value: 24. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10128 | float | RD | Min. value: 25. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10130 | float | RD | Min. value: 26. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10132 | float | RD | Min. value: 27. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10134 | float | RD | Min. value: 28. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10136 | float | RD | Min. value: 29. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10138 | float | RD | Min. value: 30. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10140 | float | RD | Min. value: 31. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10142 | float | RD | Min. value: 32. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10144 | float | RD | Min. value: 33. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10146 | float | RD | Min. value: 34. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10148 | float | RD | Min. value: 35. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10150 | float | RD | Min. value: 36. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10152 | float | RD | Min. value: 37. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10154 | float | RD | Min. value: 38. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10156 | float | RD | Min. value: 39. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 10158 | float | RD | Min. value: 40. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 14010 | short (x10) | RD | Min. value: 1. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 14011 | short (x10) | RD | Min. value: 3. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 14012 | short (x10) | RD | Min. value: 5. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 14013 | short (x10) | RD | Min. value: 7. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 14014 | short (x10) | RD | Min. value: 9. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 14015 | short (x10) | RD | Min. value: 11. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 14016 | short (x10) | RD | Min. value: 13. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 14017 | short (x10) | RD | Min. value: 15. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 14018 | short (x10) | RD | Min. value: 17. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 14019 | short (x10) | RD | Min. value: 19. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 14020 | short (x10) | RD | Min. value: 21. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 14021 | short (x10) | RD | Min. value: 23. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 14022 | short (x10) | RD | Min. value: 25. harmonic voltage L1 | V
Minimalwerte, Fourieranalyse | 46 | 14023 | short (x10) | RD | Min. value: 1. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 14024 | short (x10) | RD | Min. value: 3. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 14025 | short (x10) | RD | Min. value: 5. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 14026 | short (x10) | RD | Min. value: 7. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 14027 | short (x10) | RD | Min. value: 9. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 14028 | short (x10) | RD | Min. value: 11. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 14029 | short (x10) | RD | Min. value: 13. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 14030 | short (x10) | RD | Min. value: 15. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 14031 | short (x10) | RD | Min. value: 17. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 14032 | short (x10) | RD | Min. value: 19. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 14033 | short (x10) | RD | Min. value: 21. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 14034 | short (x10) | RD | Min. value: 23. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 14035 | short (x10) | RD | Min. value: 25. harmonic voltage L2 | V
Minimalwerte, Fourieranalyse | 46 | 14036 | short (x10) | RD | Min. value: 1. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 14037 | short (x10) | RD | Min. value: 3. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 14038 | short (x10) | RD | Min. value: 5. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 14039 | short (x10) | RD | Min. value: 7. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 14040 | short (x10) | RD | Min. value: 9. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 14041 | short (x10) | RD | Min. value: 11. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 14042 | short (x10) | RD | Min. value: 13. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 14043 | short (x10) | RD | Min. value: 15. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 14044 | short (x10) | RD | Min. value: 17. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 14045 | short (x10) | RD | Min. value: 19. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 14046 | short (x10) | RD | Min. value: 21. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 14047 | short (x10) | RD | Min. value: 23. harmonic voltage L3 | V
Minimalwerte, Fourieranalyse | 46 | 14048 | short (x10) | RD | Min. value: 25. harmonic voltage L3 | V
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4220 | uint | RD | UTC timestamp, min. value: 1. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4222 | uint | RD | UTC timestamp, min. value: 3. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4224 | uint | RD | UTC timestamp, min. value: 5. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4226 | uint | RD | UTC timestamp, min. value: 7. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4228 | uint | RD | UTC timestamp, min. value: 9. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4230 | uint | RD | UTC timestamp, min. value: 11. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4232 | uint | RD | UTC timestamp, min. value: 13. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4234 | uint | RD | UTC timestamp, min. value: 15. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4236 | uint | RD | UTC timestamp, min. value: 17. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4238 | uint | RD | UTC timestamp, min. value: 19. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4240 | uint | RD | UTC timestamp, min. value: 21. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4242 | uint | RD | UTC timestamp, min. value: 23. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4244 | uint | RD | UTC timestamp, min. value: 25. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4246 | uint | RD | UTC timestamp, min. value: 1. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4248 | uint | RD | UTC timestamp, min. value: 3. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4250 | uint | RD | UTC timestamp, min. value: 5. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4252 | uint | RD | UTC timestamp, min. value: 7. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4254 | uint | RD | UTC timestamp, min. value: 9. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4256 | uint | RD | UTC timestamp, min. value: 11. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4258 | uint | RD | UTC timestamp, min. value: 13. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4260 | uint | RD | UTC timestamp, min. value: 15. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4262 | uint | RD | UTC timestamp, min. value: 17. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4264 | uint | RD | UTC timestamp, min. value: 19. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4266 | uint | RD | UTC timestamp, min. value: 21. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4268 | uint | RD | UTC timestamp, min. value: 23. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4270 | uint | RD | UTC timestamp, min. value: 25. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4272 | uint | RD | UTC timestamp, min. value: 1. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4274 | uint | RD | UTC timestamp, min. value: 3. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4276 | uint | RD | UTC timestamp, min. value: 5. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4278 | uint | RD | UTC timestamp, min. value: 7. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4280 | uint | RD | UTC timestamp, min. value: 9. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4282 | uint | RD | UTC timestamp, min. value: 11. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4284 | uint | RD | UTC timestamp, min. value: 13. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4286 | uint | RD | UTC timestamp, min. value: 15. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4288 | uint | RD | UTC timestamp, min. value: 17. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4290 | uint | RD | UTC timestamp, min. value: 19. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4292 | uint | RD | UTC timestamp, min. value: 21. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4294 | uint | RD | UTC timestamp, min. value: 23. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 4296 | uint | RD | UTC timestamp, min. value: 25. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10160 | uint | RD | UTC timestamp, min. value: 1. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10162 | uint | RD | UTC timestamp, min. value: 2. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10164 | uint | RD | UTC timestamp, min. value: 3. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10166 | uint | RD | UTC timestamp, min. value: 4. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10168 | uint | RD | UTC timestamp, min. value: 5. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10170 | uint | RD | UTC timestamp, min. value: 6. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10172 | uint | RD | UTC timestamp, min. value: 7. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10174 | uint | RD | UTC timestamp, min. value: 8. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10176 | uint | RD | UTC timestamp, min. value: 9. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10178 | uint | RD | UTC timestamp, min. value: 10. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10180 | uint | RD | UTC timestamp, min. value: 11. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10182 | uint | RD | UTC timestamp, min. value: 12. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10184 | uint | RD | UTC timestamp, min. value: 13. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10186 | uint | RD | UTC timestamp, min. value: 14. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10188 | uint | RD | UTC timestamp, min. value: 15. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10190 | uint | RD | UTC timestamp, min. value: 16. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10192 | uint | RD | UTC timestamp, min. value: 17. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10194 | uint | RD | UTC timestamp, min. value: 18. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10196 | uint | RD | UTC timestamp, min. value: 19. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10198 | uint | RD | UTC timestamp, min. value: 20. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10200 | uint | RD | UTC timestamp, min. value: 21. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10202 | uint | RD | UTC timestamp, min. value: 22. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10204 | uint | RD | UTC timestamp, min. value: 23. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10206 | uint | RD | UTC timestamp, min. value: 24. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10208 | uint | RD | UTC timestamp, min. value: 25. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10210 | uint | RD | UTC timestamp, min. value: 26. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10212 | uint | RD | UTC timestamp, min. value: 27. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10214 | uint | RD | UTC timestamp, min. value: 28. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10216 | uint | RD | UTC timestamp, min. value: 29. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10218 | uint | RD | UTC timestamp, min. value: 30. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10220 | uint | RD | UTC timestamp, min. value: 31. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10222 | uint | RD | UTC timestamp, min. value: 32. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10224 | uint | RD | UTC timestamp, min. value: 33. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10226 | uint | RD | UTC timestamp, min. value: 34. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10228 | uint | RD | UTC timestamp, min. value: 35. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10230 | uint | RD | UTC timestamp, min. value: 36. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10232 | uint | RD | UTC timestamp, min. value: 37. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10234 | uint | RD | UTC timestamp, min. value: 38. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10236 | uint | RD | UTC timestamp, min. value: 39. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10238 | uint | RD | UTC timestamp, min. value: 40. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10240 | uint | RD | UTC timestamp, min. value: 1. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10242 | uint | RD | UTC timestamp, min. value: 2. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10244 | uint | RD | UTC timestamp, min. value: 3. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10246 | uint | RD | UTC timestamp, min. value: 4. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10248 | uint | RD | UTC timestamp, min. value: 5. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10250 | uint | RD | UTC timestamp, min. value: 6. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10252 | uint | RD | UTC timestamp, min. value: 7. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10254 | uint | RD | UTC timestamp, min. value: 8. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10256 | uint | RD | UTC timestamp, min. value: 9. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10258 | uint | RD | UTC timestamp, min. value: 10. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10260 | uint | RD | UTC timestamp, min. value: 11. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10262 | uint | RD | UTC timestamp, min. value: 12. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10264 | uint | RD | UTC timestamp, min. value: 13. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10266 | uint | RD | UTC timestamp, min. value: 14. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10268 | uint | RD | UTC timestamp, min. value: 15. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10270 | uint | RD | UTC timestamp, min. value: 16. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10272 | uint | RD | UTC timestamp, min. value: 17. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10274 | uint | RD | UTC timestamp, min. value: 18. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10276 | uint | RD | UTC timestamp, min. value: 19. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10278 | uint | RD | UTC timestamp, min. value: 20. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10280 | uint | RD | UTC timestamp, min. value: 21. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10282 | uint | RD | UTC timestamp, min. value: 22. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10284 | uint | RD | UTC timestamp, min. value: 23. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10286 | uint | RD | UTC timestamp, min. value: 24. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10288 | uint | RD | UTC timestamp, min. value: 25. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10290 | uint | RD | UTC timestamp, min. value: 26. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10292 | uint | RD | UTC timestamp, min. value: 27. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10294 | uint | RD | UTC timestamp, min. value: 28. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10296 | uint | RD | UTC timestamp, min. value: 29. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10298 | uint | RD | UTC timestamp, min. value: 30. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10300 | uint | RD | UTC timestamp, min. value: 31. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10302 | uint | RD | UTC timestamp, min. value: 32. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10304 | uint | RD | UTC timestamp, min. value: 33. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10306 | uint | RD | UTC timestamp, min. value: 34. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10308 | uint | RD | UTC timestamp, min. value: 35. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10310 | uint | RD | UTC timestamp, min. value: 36. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10312 | uint | RD | UTC timestamp, min. value: 37. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10314 | uint | RD | UTC timestamp, min. value: 38. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10316 | uint | RD | UTC timestamp, min. value: 39. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10318 | uint | RD | UTC timestamp, min. value: 40. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10320 | uint | RD | UTC timestamp, min. value: 1. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10322 | uint | RD | UTC timestamp, min. value: 2. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10324 | uint | RD | UTC timestamp, min. value: 3. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10326 | uint | RD | UTC timestamp, min. value: 4. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10328 | uint | RD | UTC timestamp, min. value: 5. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10330 | uint | RD | UTC timestamp, min. value: 6. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10332 | uint | RD | UTC timestamp, min. value: 7. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10334 | uint | RD | UTC timestamp, min. value: 8. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10336 | uint | RD | UTC timestamp, min. value: 9. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10338 | uint | RD | UTC timestamp, min. value: 10. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10340 | uint | RD | UTC timestamp, min. value: 11. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10342 | uint | RD | UTC timestamp, min. value: 12. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10344 | uint | RD | UTC timestamp, min. value: 13. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10346 | uint | RD | UTC timestamp, min. value: 14. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10348 | uint | RD | UTC timestamp, min. value: 15. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10350 | uint | RD | UTC timestamp, min. value: 16. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10352 | uint | RD | UTC timestamp, min. value: 17. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10354 | uint | RD | UTC timestamp, min. value: 18. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10356 | uint | RD | UTC timestamp, min. value: 19. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10358 | uint | RD | UTC timestamp, min. value: 20. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10360 | uint | RD | UTC timestamp, min. value: 21. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10362 | uint | RD | UTC timestamp, min. value: 22. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10364 | uint | RD | UTC timestamp, min. value: 23. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10366 | uint | RD | UTC timestamp, min. value: 24. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10368 | uint | RD | UTC timestamp, min. value: 25. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10370 | uint | RD | UTC timestamp, min. value: 26. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10372 | uint | RD | UTC timestamp, min. value: 27. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10374 | uint | RD | UTC timestamp, min. value: 28. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10376 | uint | RD | UTC timestamp, min. value: 29. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10378 | uint | RD | UTC timestamp, min. value: 30. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10380 | uint | RD | UTC timestamp, min. value: 31. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10382 | uint | RD | UTC timestamp, min. value: 32. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10384 | uint | RD | UTC timestamp, min. value: 33. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10386 | uint | RD | UTC timestamp, min. value: 34. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10388 | uint | RD | UTC timestamp, min. value: 35. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10390 | uint | RD | UTC timestamp, min. value: 36. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10392 | uint | RD | UTC timestamp, min. value: 37. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10394 | uint | RD | UTC timestamp, min. value: 38. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10396 | uint | RD | UTC timestamp, min. value: 39. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, Fourieranalyse | 48 | 10398 | uint | RD | UTC timestamp, min. value: 40. harmonic voltage L3 | s
Gleitende Mittelwerte, Fourieranalyse | 49 | 2058 | float | RD | Mean value: 1. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2060 | float | RD | Mean value: 3. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2062 | float | RD | Mean value: 5. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2064 | float | RD | Mean value: 7. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2066 | float | RD | Mean value: 9. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2068 | float | RD | Mean value: 11. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2070 | float | RD | Mean value: 13. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2072 | float | RD | Mean value: 15. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2074 | float | RD | Mean value: 17. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2076 | float | RD | Mean value: 19. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2078 | float | RD | Mean value: 21. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2080 | float | RD | Mean value: 23. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2082 | float | RD | Mean value: 25. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2084 | float | RD | Mean value: 1. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2086 | float | RD | Mean value: 3. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2088 | float | RD | Mean value: 5. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2090 | float | RD | Mean value: 7. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2092 | float | RD | Mean value: 9. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2094 | float | RD | Mean value: 11. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2096 | float | RD | Mean value: 13. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2098 | float | RD | Mean value: 15. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2100 | float | RD | Mean value: 17. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2102 | float | RD | Mean value: 19. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2104 | float | RD | Mean value: 21. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2106 | float | RD | Mean value: 23. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2108 | float | RD | Mean value: 25. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2110 | float | RD | Mean value: 1. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2112 | float | RD | Mean value: 3. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2114 | float | RD | Mean value: 5. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2116 | float | RD | Mean value: 7. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2118 | float | RD | Mean value: 9. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2120 | float | RD | Mean value: 11. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2122 | float | RD | Mean value: 13. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2124 | float | RD | Mean value: 15. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2126 | float | RD | Mean value: 17. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2128 | float | RD | Mean value: 19. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2130 | float | RD | Mean value: 21. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2132 | float | RD | Mean value: 23. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2134 | float | RD | Mean value: 25. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 2136 | float | RD | Mean value: 1. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2138 | float | RD | Mean value: 3. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2140 | float | RD | Mean value: 5. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2142 | float | RD | Mean value: 7. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2144 | float | RD | Mean value: 9. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2146 | float | RD | Mean value: 11. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2148 | float | RD | Mean value: 13. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2150 | float | RD | Mean value: 15. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2152 | float | RD | Mean value: 17. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2154 | float | RD | Mean value: 19. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2156 | float | RD | Mean value: 21. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2158 | float | RD | Mean value: 23. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2160 | float | RD | Mean value: 25. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2162 | float | RD | Mean value: 1. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2164 | float | RD | Mean value: 3. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2166 | float | RD | Mean value: 5. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2168 | float | RD | Mean value: 7. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2170 | float | RD | Mean value: 9. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2172 | float | RD | Mean value: 11. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2174 | float | RD | Mean value: 13. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2176 | float | RD | Mean value: 15. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2178 | float | RD | Mean value: 17. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2180 | float | RD | Mean value: 19. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2182 | float | RD | Mean value: 21. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2184 | float | RD | Mean value: 23. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2186 | float | RD | Mean value: 25. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2188 | float | RD | Mean value: 1. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2190 | float | RD | Mean value: 3. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2192 | float | RD | Mean value: 5. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2194 | float | RD | Mean value: 7. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2196 | float | RD | Mean value: 9. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2198 | float | RD | Mean value: 11. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2200 | float | RD | Mean value: 13. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2202 | float | RD | Mean value: 15. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2204 | float | RD | Mean value: 17. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2206 | float | RD | Mean value: 19. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2208 | float | RD | Mean value: 21. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2210 | float | RD | Mean value: 23. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 2212 | float | RD | Mean value: 25. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8480 | float | RD | Mean value: 1. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8482 | float | RD | Mean value: 2. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8484 | float | RD | Mean value: 3. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8486 | float | RD | Mean value: 4. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8488 | float | RD | Mean value: 5. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8490 | float | RD | Mean value: 6. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8492 | float | RD | Mean value: 7. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8494 | float | RD | Mean value: 8. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8496 | float | RD | Mean value: 9. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8498 | float | RD | Mean value: 10. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8500 | float | RD | Mean value: 11. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8502 | float | RD | Mean value: 12. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8504 | float | RD | Mean value: 13. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8506 | float | RD | Mean value: 14. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8508 | float | RD | Mean value: 15. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8510 | float | RD | Mean value: 16. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8512 | float | RD | Mean value: 17. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8514 | float | RD | Mean value: 18. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8516 | float | RD | Mean value: 19. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8518 | float | RD | Mean value: 20. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8520 | float | RD | Mean value: 21. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8522 | float | RD | Mean value: 22. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8524 | float | RD | Mean value: 23. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8526 | float | RD | Mean value: 24. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8528 | float | RD | Mean value: 25. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8530 | float | RD | Mean value: 26. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8532 | float | RD | Mean value: 27. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8534 | float | RD | Mean value: 28. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8536 | float | RD | Mean value: 29. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8538 | float | RD | Mean value: 30. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8540 | float | RD | Mean value: 31. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8542 | float | RD | Mean value: 32. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8544 | float | RD | Mean value: 33. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8546 | float | RD | Mean value: 34. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8548 | float | RD | Mean value: 35. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8550 | float | RD | Mean value: 36. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8552 | float | RD | Mean value: 37. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8554 | float | RD | Mean value: 38. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8556 | float | RD | Mean value: 39. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8558 | float | RD | Mean value: 40. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8560 | float | RD | Mean value: 1. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8562 | float | RD | Mean value: 2. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8564 | float | RD | Mean value: 3. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8566 | float | RD | Mean value: 4. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8568 | float | RD | Mean value: 5. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8570 | float | RD | Mean value: 6. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8572 | float | RD | Mean value: 7. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8574 | float | RD | Mean value: 8. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8576 | float | RD | Mean value: 9. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8578 | float | RD | Mean value: 10. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8580 | float | RD | Mean value: 11. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8582 | float | RD | Mean value: 12. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8584 | float | RD | Mean value: 13. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8586 | float | RD | Mean value: 14. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8588 | float | RD | Mean value: 15. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8590 | float | RD | Mean value: 16. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8592 | float | RD | Mean value: 17. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8594 | float | RD | Mean value: 18. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8596 | float | RD | Mean value: 19. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8598 | float | RD | Mean value: 20. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8600 | float | RD | Mean value: 21. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8602 | float | RD | Mean value: 22. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8604 | float | RD | Mean value: 23. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8606 | float | RD | Mean value: 24. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8608 | float | RD | Mean value: 25. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8610 | float | RD | Mean value: 26. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8612 | float | RD | Mean value: 27. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8614 | float | RD | Mean value: 28. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8616 | float | RD | Mean value: 29. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8618 | float | RD | Mean value: 30. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8620 | float | RD | Mean value: 31. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8622 | float | RD | Mean value: 32. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8624 | float | RD | Mean value: 33. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8626 | float | RD | Mean value: 34. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8628 | float | RD | Mean value: 35. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8630 | float | RD | Mean value: 36. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8632 | float | RD | Mean value: 37. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8634 | float | RD | Mean value: 38. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8636 | float | RD | Mean value: 39. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8638 | float | RD | Mean value: 40. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8640 | float | RD | Mean value: 1. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8642 | float | RD | Mean value: 2. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8644 | float | RD | Mean value: 3. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8646 | float | RD | Mean value: 4. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8648 | float | RD | Mean value: 5. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8650 | float | RD | Mean value: 6. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8652 | float | RD | Mean value: 7. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8654 | float | RD | Mean value: 8. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8656 | float | RD | Mean value: 9. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8658 | float | RD | Mean value: 10. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8660 | float | RD | Mean value: 11. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8662 | float | RD | Mean value: 12. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8664 | float | RD | Mean value: 13. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8666 | float | RD | Mean value: 14. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8668 | float | RD | Mean value: 15. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8670 | float | RD | Mean value: 16. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8672 | float | RD | Mean value: 17. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8674 | float | RD | Mean value: 18. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8676 | float | RD | Mean value: 19. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8678 | float | RD | Mean value: 20. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8680 | float | RD | Mean value: 21. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8682 | float | RD | Mean value: 22. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8684 | float | RD | Mean value: 23. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8686 | float | RD | Mean value: 24. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8688 | float | RD | Mean value: 25. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8690 | float | RD | Mean value: 26. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8692 | float | RD | Mean value: 27. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8694 | float | RD | Mean value: 28. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8696 | float | RD | Mean value: 29. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8698 | float | RD | Mean value: 30. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8700 | float | RD | Mean value: 31. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8702 | float | RD | Mean value: 32. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8704 | float | RD | Mean value: 33. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8706 | float | RD | Mean value: 34. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8708 | float | RD | Mean value: 35. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8710 | float | RD | Mean value: 36. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8712 | float | RD | Mean value: 37. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8714 | float | RD | Mean value: 38. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8716 | float | RD | Mean value: 39. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8718 | float | RD | Mean value: 40. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 8720 | float | RD | Mean value: 1. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8722 | float | RD | Mean value: 2. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8724 | float | RD | Mean value: 3. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8726 | float | RD | Mean value: 4. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8728 | float | RD | Mean value: 5. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8730 | float | RD | Mean value: 6. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8732 | float | RD | Mean value: 7. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8734 | float | RD | Mean value: 8. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8736 | float | RD | Mean value: 9. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8738 | float | RD | Mean value: 10. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8740 | float | RD | Mean value: 11. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8742 | float | RD | Mean value: 12. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8744 | float | RD | Mean value: 13. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8746 | float | RD | Mean value: 14. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8748 | float | RD | Mean value: 15. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8750 | float | RD | Mean value: 16. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8752 | float | RD | Mean value: 17. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8754 | float | RD | Mean value: 18. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8756 | float | RD | Mean value: 19. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8758 | float | RD | Mean value: 20. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8760 | float | RD | Mean value: 21. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8762 | float | RD | Mean value: 22. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8764 | float | RD | Mean value: 23. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8766 | float | RD | Mean value: 24. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8768 | float | RD | Mean value: 25. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8770 | float | RD | Mean value: 26. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8772 | float | RD | Mean value: 27. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8774 | float | RD | Mean value: 28. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8776 | float | RD | Mean value: 29. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8778 | float | RD | Mean value: 30. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8780 | float | RD | Mean value: 31. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8782 | float | RD | Mean value: 32. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8784 | float | RD | Mean value: 33. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8786 | float | RD | Mean value: 34. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8788 | float | RD | Mean value: 35. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8790 | float | RD | Mean value: 36. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8792 | float | RD | Mean value: 37. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8794 | float | RD | Mean value: 38. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8796 | float | RD | Mean value: 39. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8798 | float | RD | Mean value: 40. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8800 | float | RD | Mean value: 1. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8802 | float | RD | Mean value: 2. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8804 | float | RD | Mean value: 3. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8806 | float | RD | Mean value: 4. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8808 | float | RD | Mean value: 5. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8810 | float | RD | Mean value: 6. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8812 | float | RD | Mean value: 7. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8814 | float | RD | Mean value: 8. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8816 | float | RD | Mean value: 9. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8818 | float | RD | Mean value: 10. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8820 | float | RD | Mean value: 11. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8822 | float | RD | Mean value: 12. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8824 | float | RD | Mean value: 13. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8826 | float | RD | Mean value: 14. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8828 | float | RD | Mean value: 15. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8830 | float | RD | Mean value: 16. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8832 | float | RD | Mean value: 17. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8834 | float | RD | Mean value: 18. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8836 | float | RD | Mean value: 19. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8838 | float | RD | Mean value: 20. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8840 | float | RD | Mean value: 21. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8842 | float | RD | Mean value: 22. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8844 | float | RD | Mean value: 23. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8846 | float | RD | Mean value: 24. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8848 | float | RD | Mean value: 25. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8850 | float | RD | Mean value: 26. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8852 | float | RD | Mean value: 27. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8854 | float | RD | Mean value: 28. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8856 | float | RD | Mean value: 29. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8858 | float | RD | Mean value: 30. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8860 | float | RD | Mean value: 31. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8862 | float | RD | Mean value: 32. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8864 | float | RD | Mean value: 33. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8866 | float | RD | Mean value: 34. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8868 | float | RD | Mean value: 35. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8870 | float | RD | Mean value: 36. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8872 | float | RD | Mean value: 37. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8874 | float | RD | Mean value: 38. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8876 | float | RD | Mean value: 39. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8878 | float | RD | Mean value: 40. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8880 | float | RD | Mean value: 1. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8882 | float | RD | Mean value: 2. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8884 | float | RD | Mean value: 3. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8886 | float | RD | Mean value: 4. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8888 | float | RD | Mean value: 5. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8890 | float | RD | Mean value: 6. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8892 | float | RD | Mean value: 7. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8894 | float | RD | Mean value: 8. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8896 | float | RD | Mean value: 9. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8898 | float | RD | Mean value: 10. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8900 | float | RD | Mean value: 11. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8902 | float | RD | Mean value: 12. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8904 | float | RD | Mean value: 13. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8906 | float | RD | Mean value: 14. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8908 | float | RD | Mean value: 15. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8910 | float | RD | Mean value: 16. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8912 | float | RD | Mean value: 17. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8914 | float | RD | Mean value: 18. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8916 | float | RD | Mean value: 19. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8918 | float | RD | Mean value: 20. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8920 | float | RD | Mean value: 21. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8922 | float | RD | Mean value: 22. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8924 | float | RD | Mean value: 23. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8926 | float | RD | Mean value: 24. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8928 | float | RD | Mean value: 25. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8930 | float | RD | Mean value: 26. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8932 | float | RD | Mean value: 27. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8934 | float | RD | Mean value: 28. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8936 | float | RD | Mean value: 29. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8938 | float | RD | Mean value: 30. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8940 | float | RD | Mean value: 31. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8942 | float | RD | Mean value: 32. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8944 | float | RD | Mean value: 33. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8946 | float | RD | Mean value: 34. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8948 | float | RD | Mean value: 35. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8950 | float | RD | Mean value: 36. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8952 | float | RD | Mean value: 37. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8954 | float | RD | Mean value: 38. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8956 | float | RD | Mean value: 39. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 8958 | float | RD | Mean value: 40. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12029 | short (x10) | RD | Mean value: 1. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12030 | short (x10) | RD | Mean value: 3. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12031 | short (x10) | RD | Mean value: 5. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12032 | short (x10) | RD | Mean value: 7. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12033 | short (x10) | RD | Mean value: 9. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12034 | short (x10) | RD | Mean value: 11. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12035 | short (x10) | RD | Mean value: 13. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12036 | short (x10) | RD | Mean value: 15. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12037 | short (x10) | RD | Mean value: 17. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12038 | short (x10) | RD | Mean value: 19. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12039 | short (x10) | RD | Mean value: 21. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12040 | short (x10) | RD | Mean value: 23. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12041 | short (x10) | RD | Mean value: 25. harmonic voltage L1 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12042 | short (x10) | RD | Mean value: 1. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12043 | short (x10) | RD | Mean value: 3. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12044 | short (x10) | RD | Mean value: 5. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12045 | short (x10) | RD | Mean value: 7. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12046 | short (x10) | RD | Mean value: 9. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12047 | short (x10) | RD | Mean value: 11. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12048 | short (x10) | RD | Mean value: 13. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12049 | short (x10) | RD | Mean value: 15. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12050 | short (x10) | RD | Mean value: 17. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12051 | short (x10) | RD | Mean value: 19. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12052 | short (x10) | RD | Mean value: 21. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12053 | short (x10) | RD | Mean value: 23. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12054 | short (x10) | RD | Mean value: 25. harmonic voltage L2 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12055 | short (x10) | RD | Mean value: 1. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12056 | short (x10) | RD | Mean value: 3. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12057 | short (x10) | RD | Mean value: 5. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12058 | short (x10) | RD | Mean value: 7. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12059 | short (x10) | RD | Mean value: 9. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12060 | short (x10) | RD | Mean value: 11. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12061 | short (x10) | RD | Mean value: 13. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12062 | short (x10) | RD | Mean value: 15. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12063 | short (x10) | RD | Mean value: 17. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12064 | short (x10) | RD | Mean value: 19. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12065 | short (x10) | RD | Mean value: 21. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12066 | short (x10) | RD | Mean value: 23. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12067 | short (x10) | RD | Mean value: 25. harmonic voltage L3 | V
Gleitende Mittelwerte, Fourieranalyse | 49 | 12068 | short (x1000) | RD | Mean value: 1. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12069 | short (x1000) | RD | Mean value: 3. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12070 | short (x1000) | RD | Mean value: 5. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12071 | short (x1000) | RD | Mean value: 7. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12072 | short (x1000) | RD | Mean value: 9. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12073 | short (x1000) | RD | Mean value: 11. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12074 | short (x1000) | RD | Mean value: 13. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12075 | short (x1000) | RD | Mean value: 15. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12076 | short (x1000) | RD | Mean value: 17. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12077 | short (x1000) | RD | Mean value: 19. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12078 | short (x1000) | RD | Mean value: 21. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12079 | short (x1000) | RD | Mean value: 23. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12080 | short (x1000) | RD | Mean value: 25. harmonic current L1 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12081 | short (x1000) | RD | Mean value: 1. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12082 | short (x1000) | RD | Mean value: 3. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12083 | short (x1000) | RD | Mean value: 5. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12084 | short (x1000) | RD | Mean value: 7. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12085 | short (x1000) | RD | Mean value: 9. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12086 | short (x1000) | RD | Mean value: 11. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12087 | short (x1000) | RD | Mean value: 13. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12088 | short (x1000) | RD | Mean value: 15. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12089 | short (x1000) | RD | Mean value: 17. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12090 | short (x1000) | RD | Mean value: 19. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12091 | short (x1000) | RD | Mean value: 21. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12092 | short (x1000) | RD | Mean value: 23. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12093 | short (x1000) | RD | Mean value: 25. harmonic current L2 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12094 | short (x1000) | RD | Mean value: 1. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12095 | short (x1000) | RD | Mean value: 3. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12096 | short (x1000) | RD | Mean value: 5. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12097 | short (x1000) | RD | Mean value: 7. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12098 | short (x1000) | RD | Mean value: 9. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12099 | short (x1000) | RD | Mean value: 11. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12100 | short (x1000) | RD | Mean value: 13. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12101 | short (x1000) | RD | Mean value: 15. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12102 | short (x1000) | RD | Mean value: 17. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12103 | short (x1000) | RD | Mean value: 19. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12104 | short (x1000) | RD | Mean value: 21. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12105 | short (x1000) | RD | Mean value: 23. harmonic current L3 | A
Gleitende Mittelwerte, Fourieranalyse | 49 | 12106 | short (x1000) | RD | Mean value: 25. harmonic current L3 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17000 | float | RD | 41. harmonic voltage L1 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17002 | float | RD | 42. harmonic voltage L1 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17004 | float | RD | 43. harmonic voltage L1 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17006 | float | RD | 44. harmonic voltage L1 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17008 | float | RD | 45. harmonic voltage L1 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17010 | float | RD | 46. harmonic voltage L1 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17012 | float | RD | 47. harmonic voltage L1 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17014 | float | RD | 48. harmonic voltage L1 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17016 | float | RD | 49. harmonic voltage L1 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17018 | float | RD | 50. harmonic voltage L1 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17020 | float | RD | 51. harmonic voltage L1 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17022 | float | RD | 52. harmonic voltage L1 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17024 | float | RD | 53. harmonic voltage L1 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17026 | float | RD | 54. harmonic voltage L1 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17028 | float | RD | 55. harmonic voltage L1 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17030 | float | RD | 56. harmonic voltage L1 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17032 | float | RD | 57. harmonic voltage L1 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17034 | float | RD | 58. harmonic voltage L1 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17036 | float | RD | 59. harmonic voltage L1 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17038 | float | RD | 60. harmonic voltage L1 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17040 | float | RD | 61. harmonic voltage L1 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17042 | float | RD | 62. harmonic voltage L1 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17044 | float | RD | 63. harmonic voltage L1 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17046 | float | RD | 64. harmonic voltage L1 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17048 | float | RD | 65. harmonic voltage L1 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17050 | float | RD | 41. harmonic voltage L2 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17052 | float | RD | 42. harmonic voltage L2 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17054 | float | RD | 43. harmonic voltage L2 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17056 | float | RD | 44. harmonic voltage L2 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17058 | float | RD | 45. harmonic voltage L2 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17060 | float | RD | 46. harmonic voltage L2 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17062 | float | RD | 47. harmonic voltage L2 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17064 | float | RD | 48. harmonic voltage L2 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17066 | float | RD | 49. harmonic voltage L2 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17068 | float | RD | 50. harmonic voltage L2 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17070 | float | RD | 51. harmonic voltage L2 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17072 | float | RD | 52. harmonic voltage L2 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17074 | float | RD | 53. harmonic voltage L2 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17076 | float | RD | 54. harmonic voltage L2 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17078 | float | RD | 55. harmonic voltage L2 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17080 | float | RD | 56. harmonic voltage L2 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17082 | float | RD | 57. harmonic voltage L2 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17084 | float | RD | 58. harmonic voltage L2 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17086 | float | RD | 59. harmonic voltage L2 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17088 | float | RD | 60. harmonic voltage L2 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17090 | float | RD | 61. harmonic voltage L2 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17092 | float | RD | 62. harmonic voltage L2 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17094 | float | RD | 63. harmonic voltage L2 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17096 | float | RD | 64. harmonic voltage L2 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17098 | float | RD | 65. harmonic voltage L2 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17100 | float | RD | 41. harmonic voltage L3 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17102 | float | RD | 42. harmonic voltage L3 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17104 | float | RD | 43. harmonic voltage L3 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17106 | float | RD | 44. harmonic voltage L3 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17108 | float | RD | 45. harmonic voltage L3 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17110 | float | RD | 46. harmonic voltage L3 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17112 | float | RD | 47. harmonic voltage L3 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17114 | float | RD | 48. harmonic voltage L3 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17116 | float | RD | 49. harmonic voltage L3 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17118 | float | RD | 50. harmonic voltage L3 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17120 | float | RD | 51. harmonic voltage L3 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17122 | float | RD | 52. harmonic voltage L3 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17124 | float | RD | 53. harmonic voltage L3 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17126 | float | RD | 54. harmonic voltage L3 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17128 | float | RD | 55. harmonic voltage L3 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17130 | float | RD | 56. harmonic voltage L3 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17132 | float | RD | 57. harmonic voltage L3 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17134 | float | RD | 58. harmonic voltage L3 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17136 | float | RD | 59. harmonic voltage L3 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17138 | float | RD | 60. harmonic voltage L3 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17140 | float | RD | 61. harmonic voltage L3 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17142 | float | RD | 62. harmonic voltage L3 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17144 | float | RD | 63. harmonic voltage L3 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17146 | float | RD | 64. harmonic voltage L3 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17148 | float | RD | 65. harmonic voltage L3 | V
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17150 | float | RD | 41. harmonic current L1 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17152 | float | RD | 42. harmonic current L1 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17154 | float | RD | 43. harmonic current L1 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17156 | float | RD | 44. harmonic current L1 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17158 | float | RD | 45. harmonic current L1 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17160 | float | RD | 46. harmonic current L1 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17162 | float | RD | 47. harmonic current L1 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17164 | float | RD | 48. harmonic current L1 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17166 | float | RD | 49. harmonic current L1 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17168 | float | RD | 50. harmonic current L1 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17170 | float | RD | 51. harmonic current L1 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17172 | float | RD | 52. harmonic current L1 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17174 | float | RD | 53. harmonic current L1 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17176 | float | RD | 54. harmonic current L1 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17178 | float | RD | 55. harmonic current L1 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17180 | float | RD | 56. harmonic current L1 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17182 | float | RD | 57. harmonic current L1 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17184 | float | RD | 58. harmonic current L1 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17186 | float | RD | 59. harmonic current L1 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17188 | float | RD | 60. harmonic current L1 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17190 | float | RD | 61. harmonic current L1 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17192 | float | RD | 62. harmonic current L1 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17194 | float | RD | 63. harmonic current L1 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17196 | float | RD | 64. harmonic current L1 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17198 | float | RD | 65. harmonic current L1 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17200 | float | RD | 41. harmonic current L2 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17202 | float | RD | 42. harmonic current L2 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17204 | float | RD | 43. harmonic current L2 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17206 | float | RD | 44. harmonic current L2 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17208 | float | RD | 45. harmonic current L2 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17210 | float | RD | 46. harmonic current L2 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17212 | float | RD | 47. harmonic current L2 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17214 | float | RD | 48. harmonic current L2 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17216 | float | RD | 49. harmonic current L2 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17218 | float | RD | 50. harmonic current L2 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17220 | float | RD | 51. harmonic current L2 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17222 | float | RD | 52. harmonic current L2 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17224 | float | RD | 53. harmonic current L2 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17226 | float | RD | 54. harmonic current L2 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17228 | float | RD | 55. harmonic current L2 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17230 | float | RD | 56. harmonic current L2 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17232 | float | RD | 57. harmonic current L2 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17234 | float | RD | 58. harmonic current L2 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17236 | float | RD | 59. harmonic current L2 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17238 | float | RD | 60. harmonic current L2 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17240 | float | RD | 61. harmonic current L2 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17242 | float | RD | 62. harmonic current L2 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17244 | float | RD | 63. harmonic current L2 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17246 | float | RD | 64. harmonic current L2 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17248 | float | RD | 65. harmonic current L2 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17250 | float | RD | 41. harmonic current L3 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17252 | float | RD | 42. harmonic current L3 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17254 | float | RD | 43. harmonic current L3 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17256 | float | RD | 44. harmonic current L3 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17258 | float | RD | 45. harmonic current L3 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17260 | float | RD | 46. harmonic current L3 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17262 | float | RD | 47. harmonic current L3 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17264 | float | RD | 48. harmonic current L3 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17266 | float | RD | 49. harmonic current L3 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17268 | float | RD | 50. harmonic current L3 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17270 | float | RD | 51. harmonic current L3 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17272 | float | RD | 52. harmonic current L3 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17274 | float | RD | 53. harmonic current L3 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17276 | float | RD | 54. harmonic current L3 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17278 | float | RD | 55. harmonic current L3 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17280 | float | RD | 56. harmonic current L3 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17282 | float | RD | 57. harmonic current L3 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17284 | float | RD | 58. harmonic current L3 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17286 | float | RD | 59. harmonic current L3 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17288 | float | RD | 60. harmonic current L3 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17290 | float | RD | 61. harmonic current L3 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17292 | float | RD | 62. harmonic current L3 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17294 | float | RD | 63. harmonic current L3 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17296 | float | RD | 64. harmonic current L3 | A
Messwerte, erweiterte Fourieranalyse (41.-65. Harmonische) | 51 | 17298 | float | RD | 65. harmonic current L3 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17600 | float | RD | Max. value: 41. harmonic voltage L1 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17602 | float | RD | Max. value: 42. harmonic voltage L1 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17604 | float | RD | Max. value: 43. harmonic voltage L1 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17606 | float | RD | Max. value: 44. harmonic voltage L1 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17608 | float | RD | Max. value: 45. harmonic voltage L1 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17610 | float | RD | Max. value: 46. harmonic voltage L1 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17612 | float | RD | Max. value: 47. harmonic voltage L1 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17614 | float | RD | Max. value: 48. harmonic voltage L1 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17616 | float | RD | Max. value: 49. harmonic voltage L1 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17618 | float | RD | Max. value: 50. harmonic voltage L1 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17620 | float | RD | Max. value: 51. harmonic voltage L1 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17622 | float | RD | Max. value: 52. harmonic voltage L1 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17624 | float | RD | Max. value: 53. harmonic voltage L1 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17626 | float | RD | Max. value: 54. harmonic voltage L1 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17628 | float | RD | Max. value: 55. harmonic voltage L1 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17630 | float | RD | Max. value: 56. harmonic voltage L1 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17632 | float | RD | Max. value: 57. harmonic voltage L1 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17634 | float | RD | Max. value: 58. harmonic voltage L1 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17636 | float | RD | Max. value: 59. harmonic voltage L1 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17638 | float | RD | Max. value: 60. harmonic voltage L1 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17640 | float | RD | Max. value: 61. harmonic voltage L1 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17642 | float | RD | Max. value: 62. harmonic voltage L1 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17644 | float | RD | Max. value: 63. harmonic voltage L1 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17646 | float | RD | Max. value: 64. harmonic voltage L1 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17648 | float | RD | Max. value: 65. harmonic voltage L1 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17650 | float | RD | Max. value: 41. harmonic voltage L2 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17652 | float | RD | Max. value: 42. harmonic current L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17654 | float | RD | Max. value: 43. harmonic current L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17656 | float | RD | Max. value: 44. harmonic current L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17658 | float | RD | Max. value: 45. harmonic current L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17660 | float | RD | Max. value: 46. harmonic current L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17662 | float | RD | Max. value: 47. harmonic current L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17664 | float | RD | Max. value: 48. harmonic current L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17666 | float | RD | Max. value: 49. harmonic current L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17668 | float | RD | Max. value: 50. harmonic current L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17670 | float | RD | Max. value: 51. harmonic current L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17672 | float | RD | Max. value: 52. harmonic current L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17674 | float | RD | Max. value: 53. harmonic current L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17676 | float | RD | Max. value: 54. harmonic current L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17678 | float | RD | Max. value: 55. harmonic current L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17680 | float | RD | Max. value: 56. harmonic current L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17682 | float | RD | Max. value: 57. harmonic current L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17684 | float | RD | Max. value: 58. harmonic current L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17686 | float | RD | Max. value: 59. harmonic current L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17688 | float | RD | Max. value: 60. harmonic current L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17690 | float | RD | Max. value: 61. harmonic current L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17692 | float | RD | Max. value: 62. harmonic current L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17694 | float | RD | Max. value: 63. harmonic current L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17696 | float | RD | Max. value: 64. harmonic current L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17698 | float | RD | Max. value: 65. harmonic current L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17700 | float | RD | Max. value: 41. harmonic voltage L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17702 | float | RD | Max. value: 42. harmonic voltage L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17704 | float | RD | Max. value: 43. harmonic voltage L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17706 | float | RD | Max. value: 44. harmonic voltage L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17708 | float | RD | Max. value: 45. harmonic voltage L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17710 | float | RD | Max. value: 46. harmonic voltage L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17712 | float | RD | Max. value: 47. harmonic voltage L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17714 | float | RD | Max. value: 48. harmonic voltage L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17716 | float | RD | Max. value: 49. harmonic voltage L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17718 | float | RD | Max. value: 50. harmonic voltage L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17720 | float | RD | Max. value: 51. harmonic voltage L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17722 | float | RD | Max. value: 52. harmonic voltage L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17724 | float | RD | Max. value: 53. harmonic voltage L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17726 | float | RD | Max. value: 54. harmonic voltage L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17728 | float | RD | Max. value: 55. harmonic voltage L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17730 | float | RD | Max. value: 56. harmonic voltage L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17732 | float | RD | Max. value: 57. harmonic voltage L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17734 | float | RD | Max. value: 58. harmonic voltage L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17736 | float | RD | Max. value: 59. harmonic voltage L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17738 | float | RD | Max. value: 60. harmonic voltage L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17740 | float | RD | Max. value: 61. harmonic voltage L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17742 | float | RD | Max. value: 62. harmonic voltage L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17744 | float | RD | Max. value: 63. harmonic voltage L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17746 | float | RD | Max. value: 64. harmonic voltage L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17748 | float | RD | Max. value: 65. harmonic voltage L3 | V
Maximalwerte, erweiterte Fourieranalyse | 52 | 17750 | float | RD | Max. value: 41. harmonic current L1 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17752 | float | RD | Max. value: 42. harmonic current L1 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17754 | float | RD | Max. value: 43. harmonic current L1 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17756 | float | RD | Max. value: 44. harmonic current L1 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17758 | float | RD | Max. value: 45. harmonic current L1 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17760 | float | RD | Max. value: 46. harmonic current L1 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17762 | float | RD | Max. value: 47. harmonic current L1 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17764 | float | RD | Max. value: 48. harmonic current L1 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17766 | float | RD | Max. value: 49. harmonic current L1 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17768 | float | RD | Max. value: 50. harmonic current L1 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17770 | float | RD | Max. value: 51. harmonic current L1 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17772 | float | RD | Max. value: 52. harmonic current L1 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17774 | float | RD | Max. value: 53. harmonic current L1 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17776 | float | RD | Max. value: 54. harmonic current L1 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17778 | float | RD | Max. value: 55. harmonic current L1 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17780 | float | RD | Max. value: 56. harmonic current L1 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17782 | float | RD | Max. value: 57. harmonic current L1 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17784 | float | RD | Max. value: 58. harmonic current L1 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17786 | float | RD | Max. value: 59. harmonic current L1 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17788 | float | RD | Max. value: 60. harmonic current L1 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17790 | float | RD | Max. value: 61. harmonic current L1 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17792 | float | RD | Max. value: 62. harmonic current L1 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17794 | float | RD | Max. value: 63. harmonic current L1 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17796 | float | RD | Max. value: 64. harmonic current L1 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17798 | float | RD | Max. value: 65. harmonic current L1 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17800 | float | RD | Max. value: 41. harmonic current L2 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17802 | float | RD | Max. value: 42. harmonic current L2 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17804 | float | RD | Max. value: 43. harmonic current L2 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17806 | float | RD | Max. value: 44. harmonic current L2 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17808 | float | RD | Max. value: 45. harmonic current L2 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17810 | float | RD | Max. value: 46. harmonic current L2 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17812 | float | RD | Max. value: 47. harmonic current L2 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17814 | float | RD | Max. value: 48. harmonic current L2 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17816 | float | RD | Max. value: 49. harmonic current L2 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17818 | float | RD | Max. value: 49. harmonic current L2 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17820 | float | RD | Max. value: 49. harmonic current L2 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17822 | float | RD | Max. value: 52. harmonic current L2 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17824 | float | RD | Max. value: 53. harmonic current L2 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17826 | float | RD | Max. value: 54. harmonic current L2 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17828 | float | RD | Max. value: 55. harmonic current L2 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17830 | float | RD | Max. value: 56. harmonic current L2 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17832 | float | RD | Max. value: 57. harmonic current L2 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17834 | float | RD | Max. value: 58. harmonic current L2 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17836 | float | RD | Max. value: 59. harmonic current L2 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17838 | float | RD | Max. value: 60. harmonic current L2 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17840 | float | RD | Max. value: 61. harmonic current L2 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17842 | float | RD | Max. value: 62. harmonic current L2 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17844 | float | RD | Max. value: 63. harmonic current L2 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17846 | float | RD | Max. value: 64. harmonic current L2 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17848 | float | RD | Max. value: 65. harmonic current L2 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17850 | float | RD | Max. value: 41. harmonic current L3 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17852 | float | RD | Max. value: 42. harmonic current L3 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17854 | float | RD | Max. value: 43. harmonic current L3 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17856 | float | RD | Max. value: 44. harmonic current L3 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17858 | float | RD | Max. value: 45. harmonic current L3 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17860 | float | RD | Max. value: 46. harmonic current L3 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17862 | float | RD | Max. value: 47. harmonic current L3 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17864 | float | RD | Max. value: 48. harmonic current L3 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17866 | float | RD | Max. value: 49. harmonic current L3 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17868 | float | RD | Max. value: 50. harmonic current L3 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17870 | float | RD | Max. value: 51. harmonic current L3 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17872 | float | RD | Max. value: 52. harmonic current L3 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17874 | float | RD | Max. value: 53. harmonic current L3 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17876 | float | RD | Max. value: 54. harmonic current L3 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17878 | float | RD | Max. value: 55. harmonic current L3 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17880 | float | RD | Max. value: 56. harmonic current L3 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17882 | float | RD | Max. value: 57. harmonic current L3 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17884 | float | RD | Max. value: 58. harmonic current L3 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17886 | float | RD | Max. value: 59. harmonic current L3 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17888 | float | RD | Max. value: 60. harmonic current L3 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17890 | float | RD | Max. value: 61. harmonic current L3 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17892 | float | RD | Max. value: 62. harmonic current L3 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17894 | float | RD | Max. value: 63. harmonic current L3 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17896 | float | RD | Max. value: 64. harmonic current L3 | A
Maximalwerte, erweiterte Fourieranalyse | 52 | 17898 | float | RD | Max. value: 65. harmonic current L3 | A
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17900 | uint | RD | UTC timestamp: max. value, 41. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17902 | uint | RD | UTC timestamp: max. value, 42. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17904 | uint | RD | UTC timestamp: max. value, 43. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17906 | uint | RD | UTC timestamp: max. value, 44. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17908 | uint | RD | UTC timestamp: max. value, 45. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17910 | uint | RD | UTC timestamp: max. value, 46. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17912 | uint | RD | UTC timestamp: max. value, 47. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17914 | uint | RD | UTC timestamp: max. value, 48. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17916 | uint | RD | UTC timestamp: max. value, 49. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17918 | uint | RD | UTC timestamp: max. value, 50. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17920 | uint | RD | UTC timestamp: max. value, 51. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17922 | uint | RD | UTC timestamp: max. value, 52. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17924 | uint | RD | UTC timestamp: max. value, 53. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17926 | uint | RD | UTC timestamp: max. value, 54. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17928 | uint | RD | UTC timestamp: max. value, 55. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17930 | uint | RD | UTC timestamp: max. value, 56. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17932 | uint | RD | UTC timestamp: max. value, 57. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17934 | uint | RD | UTC timestamp: max. value, 58. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17936 | uint | RD | UTC timestamp: max. value, 59. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17938 | uint | RD | UTC timestamp: max. value, 60. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17940 | uint | RD | UTC timestamp: max. value, 61. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17942 | uint | RD | UTC timestamp: max. value, 62. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17944 | uint | RD | UTC timestamp: max. value, 63. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17946 | uint | RD | UTC timestamp: max. value, 64. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17948 | uint | RD | UTC timestamp: max. value, 65. harmonic voltage L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17950 | uint | RD | UTC timestamp: max. value, 41. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17952 | uint | RD | UTC timestamp: max. value, 42. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17954 | uint | RD | UTC timestamp: max. value, 43. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17956 | uint | RD | UTC timestamp: max. value, 44. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17958 | uint | RD | UTC timestamp: max. value, 45. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17960 | uint | RD | UTC timestamp: max. value, 46. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17962 | uint | RD | UTC timestamp: max. value, 47. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17964 | uint | RD | UTC timestamp: max. value, 48. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17966 | uint | RD | UTC timestamp: max. value, 49. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17968 | uint | RD | UTC timestamp: max. value, 50. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17970 | uint | RD | UTC timestamp: max. value, 51. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17972 | uint | RD | UTC timestamp: max. value, 52. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17974 | uint | RD | UTC timestamp: max. value, 53. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17976 | uint | RD | UTC timestamp: max. value, 54. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17978 | uint | RD | UTC timestamp: max. value, 55. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17980 | uint | RD | UTC timestamp: max. value, 56. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17982 | uint | RD | UTC timestamp: max. value, 57. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17984 | uint | RD | UTC timestamp: max. value, 58. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17986 | uint | RD | UTC timestamp: max. value, 59. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17988 | uint | RD | UTC timestamp: max. value, 60. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17990 | uint | RD | UTC timestamp: max. value, 61. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17992 | uint | RD | UTC timestamp: max. value, 62. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17994 | uint | RD | UTC timestamp: max. value, 63. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17996 | uint | RD | UTC timestamp: max. value, 64. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 17998 | uint | RD | UTC timestamp: max. value, 65. harmonic voltage L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18000 | uint | RD | UTC timestamp: max. value, 41. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18002 | uint | RD | UTC timestamp: max. value, 42. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18004 | uint | RD | UTC timestamp: max. value, 43. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18006 | uint | RD | UTC timestamp: max. value, 44. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18008 | uint | RD | UTC timestamp: max. value, 45. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18010 | uint | RD | UTC timestamp: max. value, 46. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18012 | uint | RD | UTC timestamp: max. value, 47. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18014 | uint | RD | UTC timestamp: max. value, 48. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18016 | uint | RD | UTC timestamp: max. value, 49. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18018 | uint | RD | UTC timestamp: max. value, 50. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18020 | uint | RD | UTC timestamp: max. value, 51. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18022 | uint | RD | UTC timestamp: max. value, 52. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18024 | uint | RD | UTC timestamp: max. value, 53. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18026 | uint | RD | UTC timestamp: max. value, 54. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18028 | uint | RD | UTC timestamp: max. value, 55. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18030 | uint | RD | UTC timestamp: max. value, 56. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18032 | uint | RD | UTC timestamp: max. value, 57. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18034 | uint | RD | UTC timestamp: max. value, 58. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18036 | uint | RD | UTC timestamp: max. value, 59. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18038 | uint | RD | UTC timestamp: max. value, 60. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18040 | uint | RD | UTC timestamp: max. value, 61. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18042 | uint | RD | UTC timestamp: max. value, 62. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18044 | uint | RD | UTC timestamp: max. value, 63. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18046 | uint | RD | UTC timestamp: max. value, 64. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18048 | uint | RD | UTC timestamp: max. value, 65. harmonic voltage L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18050 | uint | RD | UTC timestamp: max. value, 41. harmonic current L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18052 | uint | RD | UTC timestamp: max. value, 42. harmonic current L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18054 | uint | RD | UTC timestamp: max. value, 43. harmonic current L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18056 | uint | RD | UTC timestamp: max. value, 44. harmonic current L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18058 | uint | RD | UTC timestamp: max. value, 45. harmonic current L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18060 | uint | RD | UTC timestamp: max. value, 46. harmonic current L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18062 | uint | RD | UTC timestamp: max. value, 47. harmonic current L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18064 | uint | RD | UTC timestamp: max. value, 48. harmonic current L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18066 | uint | RD | UTC timestamp: max. value, 49. harmonic current L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18068 | uint | RD | UTC timestamp: max. value, 50. harmonic current L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18070 | uint | RD | UTC timestamp: max. value, 51. harmonic current L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18072 | uint | RD | UTC timestamp: max. value, 52. harmonic current L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18074 | uint | RD | UTC timestamp: max. value, 53. harmonic current L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18076 | uint | RD | UTC timestamp: max. value, 54. harmonic current L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18078 | uint | RD | UTC timestamp: max. value, 55. harmonic current L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18080 | uint | RD | UTC timestamp: max. value, 56. harmonic current L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18082 | uint | RD | UTC timestamp: max. value, 57. harmonic current L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18084 | uint | RD | UTC timestamp: max. value, 58. harmonic current L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18086 | uint | RD | UTC timestamp: max. value, 59. harmonic current L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18088 | uint | RD | UTC timestamp: max. value, 60. harmonic current L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18090 | uint | RD | UTC timestamp: max. value, 61. harmonic current L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18092 | uint | RD | UTC timestamp: max. value, 62. harmonic current L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18094 | uint | RD | UTC timestamp: max. value, 63. harmonic current L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18096 | uint | RD | UTC timestamp: max. value, 64. harmonic current L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18098 | uint | RD | UTC timestamp: max. value, 65. harmonic current L1 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18100 | uint | RD | UTC timestamp: max. value, 41. harmonic current L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18102 | uint | RD | UTC timestamp: max. value, 42. harmonic current L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18104 | uint | RD | UTC timestamp: max. value, 43. harmonic current L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18106 | uint | RD | UTC timestamp: max. value, 44. harmonic current L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18108 | uint | RD | UTC timestamp: max. value, 45. harmonic current L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18110 | uint | RD | UTC timestamp: max. value, 46. harmonic current L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18112 | uint | RD | UTC timestamp: max. value, 47. harmonic current L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18114 | uint | RD | UTC timestamp: max. value, 48. harmonic current L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18116 | uint | RD | UTC timestamp: max. value, 49. harmonic current L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18118 | uint | RD | UTC timestamp: max. value, 50. harmonic current L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18120 | uint | RD | UTC timestamp: max. value, 51. harmonic current L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18122 | uint | RD | UTC timestamp: max. value, 52. harmonic current L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18124 | uint | RD | UTC timestamp: max. value, 53. harmonic current L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18126 | uint | RD | UTC timestamp: max. value, 54. harmonic current L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18128 | uint | RD | UTC timestamp: max. value, 55. harmonic current L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18130 | uint | RD | UTC timestamp: max. value, 56. harmonic current L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18132 | uint | RD | UTC timestamp: max. value, 57. harmonic current L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18134 | uint | RD | UTC timestamp: max. value, 58. harmonic current L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18136 | uint | RD | UTC timestamp: max. value, 59. harmonic current L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18138 | uint | RD | UTC timestamp: max. value, 60. harmonic current L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18140 | uint | RD | UTC timestamp: max. value, 61. harmonic current L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18142 | uint | RD | UTC timestamp: max. value, 62. harmonic current L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18144 | uint | RD | UTC timestamp: max. value, 63. harmonic current L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18146 | uint | RD | UTC timestamp: max. value, 64. harmonic current L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18148 | uint | RD | UTC timestamp: max. value, 65. harmonic current L2 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18150 | uint | RD | UTC timestamp: max. value, 41. harmonic current L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18152 | uint | RD | UTC timestamp: max. value, 42. harmonic current L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18154 | uint | RD | UTC timestamp: max. value, 43. harmonic current L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18156 | uint | RD | UTC timestamp: max. value, 44. harmonic current L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18158 | uint | RD | UTC timestamp: max. value, 45. harmonic current L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18160 | uint | RD | UTC timestamp: max. value, 46. harmonic current L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18162 | uint | RD | UTC timestamp: max. value, 47. harmonic current L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18164 | uint | RD | UTC timestamp: max. value, 48. harmonic current L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18166 | uint | RD | UTC timestamp: max. value, 49. harmonic current L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18168 | uint | RD | UTC timestamp: max. value, 50. harmonic current L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18170 | uint | RD | UTC timestamp: max. value, 51. harmonic current L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18172 | uint | RD | UTC timestamp: max. value, 52. harmonic current L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18174 | uint | RD | UTC timestamp: max. value, 53. harmonic current L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18176 | uint | RD | UTC timestamp: max. value, 54. harmonic current L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18178 | uint | RD | UTC timestamp: max. value, 55. harmonic current L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18180 | uint | RD | UTC timestamp: max. value, 56. harmonic current L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18182 | uint | RD | UTC timestamp: max. value, 57. harmonic current L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18184 | uint | RD | UTC timestamp: max. value, 58. harmonic current L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18186 | uint | RD | UTC timestamp: max. value, 59. harmonic current L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18188 | uint | RD | UTC timestamp: max. value, 60. harmonic current L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18190 | uint | RD | UTC timestamp: max. value, 61. harmonic current L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18192 | uint | RD | UTC timestamp: max. value, 62. harmonic current L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18194 | uint | RD | UTC timestamp: max. value, 63. harmonic current L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18196 | uint | RD | UTC timestamp: max. value, 64. harmonic current L3 | s
Maximalwerte, Zeitstempel, erweiterte Fourieranalyse | 53 | 18198 | uint | RD | UTC timestamp: max. value, 65. harmonic current L3 | s
Minimalwerte, erweiterte Fourieranalyse | 54 | 18200 | float | RD | Min. value, 41. harmonic voltage L1 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18202 | float | RD | Min. value, 42. harmonic voltage L1 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18204 | float | RD | Min. value, 43. harmonic voltage L1 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18206 | float | RD | Min. value, 44. harmonic voltage L1 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18208 | float | RD | Min. value, 45. harmonic voltage L1 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18210 | float | RD | Min. value, 46. harmonic voltage L1 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18212 | float | RD | Min. value, 47. harmonic voltage L1 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18214 | float | RD | Min. value, 48. harmonic voltage L1 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18216 | float | RD | Min. value, 49. harmonic voltage L1 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18218 | float | RD | Min. value, 50. harmonic voltage L1 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18220 | float | RD | Min. value, 51. harmonic voltage L1 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18222 | float | RD | Min. value, 52. harmonic voltage L1 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18224 | float | RD | Min. value, 53. harmonic voltage L1 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18226 | float | RD | Min. value, 54. harmonic voltage L1 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18228 | float | RD | Min. value, 55. harmonic voltage L1 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18230 | float | RD | Min. value, 56. harmonic voltage L1 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18232 | float | RD | Min. value, 57. harmonic voltage L1 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18234 | float | RD | Min. value, 58. harmonic voltage L1 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18236 | float | RD | Min. value, 59. harmonic voltage L1 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18238 | float | RD | Min. value, 60. harmonic voltage L1 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18240 | float | RD | Min. value, 61. harmonic voltage L1 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18242 | float | RD | Min. value, 62. harmonic voltage L1 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18244 | float | RD | Min. value, 63. harmonic voltage L1 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18246 | float | RD | Min. value, 64. harmonic voltage L1 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18248 | float | RD | Min. value, 65. harmonic voltage L1 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18250 | float | RD | Min. value, 41. harmonic voltage L2 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18252 | float | RD | Min. value, 42. harmonic voltage L2 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18254 | float | RD | Min. value, 43. harmonic voltage L2 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18256 | float | RD | Min. value, 44. harmonic voltage L2 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18258 | float | RD | Min. value, 45. harmonic voltage L2 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18260 | float | RD | Min. value, 46. harmonic voltage L2 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18262 | float | RD | Min. value, 47. harmonic voltage L2 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18264 | float | RD | Min. value, 48. harmonic voltage L2 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18266 | float | RD | Min. value, 49. harmonic voltage L2 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18268 | float | RD | Min. value, 50. harmonic voltage L2 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18270 | float | RD | Min. value, 51. harmonic voltage L2 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18272 | float | RD | Min. value, 52. harmonic voltage L2 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18274 | float | RD | Min. value, 53. harmonic voltage L2 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18276 | float | RD | Min. value, 54. harmonic voltage L2 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18278 | float | RD | Min. value, 55. harmonic voltage L2 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18280 | float | RD | Min. value, 56. harmonic voltage L2 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18282 | float | RD | Min. value, 57. harmonic voltage L2 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18284 | float | RD | Min. value, 58. harmonic voltage L2 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18286 | float | RD | Min. value, 59. harmonic voltage L2 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18288 | float | RD | Min. value, 60. harmonic voltage L2 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18290 | float | RD | Min. value, 61. harmonic voltage L2 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18292 | float | RD | Min. value, 62. harmonic voltage L2 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18294 | float | RD | Min. value, 63. harmonic voltage L2 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18296 | float | RD | Min. value, 64. harmonic voltage L2 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18298 | float | RD | Min. value, 65. harmonic voltage L2 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18300 | float | RD | Min. value, 41. harmonic voltage L3 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18302 | float | RD | Min. value, 42. harmonic voltage L3 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18304 | float | RD | Min. value, 43. harmonic voltage L3 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18306 | float | RD | Min. value, 44. harmonic voltage L3 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18308 | float | RD | Min. value, 45. harmonic voltage L3 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18310 | float | RD | Min. value, 46. harmonic voltage L3 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18312 | float | RD | Min. value, 47. harmonic voltage L3 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18314 | float | RD | Min. value, 48. harmonic voltage L3 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18316 | float | RD | Min. value, 49. harmonic voltage L3 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18318 | float | RD | Min. value, 50. harmonic voltage L3 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18320 | float | RD | Min. value, 51. harmonic voltage L3 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18322 | float | RD | Min. value, 52. harmonic voltage L3 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18324 | float | RD | Min. value, 53. harmonic voltage L3 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18326 | float | RD | Min. value, 54. harmonic voltage L3 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18328 | float | RD | Min. value, 55. harmonic voltage L3 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18330 | float | RD | Min. value, 56. harmonic voltage L3 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18332 | float | RD | Min. value, 57. harmonic voltage L3 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18334 | float | RD | Min. value, 58. harmonic voltage L3 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18336 | float | RD | Min. value, 59. harmonic voltage L3 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18338 | float | RD | Min. value, 60. harmonic voltage L3 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18340 | float | RD | Min. value, 61. harmonic voltage L3 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18342 | float | RD | Min. value, 62. harmonic voltage L3 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18344 | float | RD | Min. value, 63. harmonic voltage L3 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18346 | float | RD | Min. value, 64. harmonic voltage L3 | V
Minimalwerte, erweiterte Fourieranalyse | 54 | 18348 | float | RD | Min. value, 65. harmonic voltage L3 | V
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18350 | uint | RD | UTC timestamp: min. value, 41. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18352 | uint | RD | UTC timestamp: min. value, 42. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18354 | uint | RD | UTC timestamp: min. value, 43. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18356 | uint | RD | UTC timestamp: min. value, 44. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18358 | uint | RD | UTC timestamp: min. value, 45. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18360 | uint | RD | UTC timestamp: min. value, 46. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18362 | uint | RD | UTC timestamp: min. value, 47. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18364 | uint | RD | UTC timestamp: min. value, 48. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18366 | uint | RD | UTC timestamp: min. value, 49. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18368 | uint | RD | UTC timestamp: min. value, 50. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18370 | uint | RD | UTC timestamp: min. value, 51. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18372 | uint | RD | UTC timestamp: min. value, 52. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18374 | uint | RD | UTC timestamp: min. value, 53. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18376 | uint | RD | UTC timestamp: min. value, 54. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18378 | uint | RD | UTC timestamp: min. value, 55. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18380 | uint | RD | UTC timestamp: min. value, 56. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18382 | uint | RD | UTC timestamp: min. value, 57. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18384 | uint | RD | UTC timestamp: min. value, 58. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18386 | uint | RD | UTC timestamp: min. value, 59. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18388 | uint | RD | UTC timestamp: min. value, 60. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18390 | uint | RD | UTC timestamp: min. value, 61. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18392 | uint | RD | UTC timestamp: min. value, 62. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18394 | uint | RD | UTC timestamp: min. value, 63. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18396 | uint | RD | UTC timestamp: min. value, 64. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18398 | uint | RD | UTC timestamp: min. value, 65. harmonic voltage L1 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18400 | uint | RD | UTC timestamp: min. value, 41. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18402 | uint | RD | UTC timestamp: min. value, 42. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18404 | uint | RD | UTC timestamp: min. value, 43. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18406 | uint | RD | UTC timestamp: min. value, 44. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18408 | uint | RD | UTC timestamp: min. value, 45. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18410 | uint | RD | UTC timestamp: min. value, 46. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18412 | uint | RD | UTC timestamp: min. value, 47. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18414 | uint | RD | UTC timestamp: min. value, 48. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18416 | uint | RD | UTC timestamp: min. value, 49. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18418 | uint | RD | UTC timestamp: min. value, 50. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18420 | uint | RD | UTC timestamp: min. value, 51. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18422 | uint | RD | UTC timestamp: min. value, 52. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18424 | uint | RD | UTC timestamp: min. value, 53. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18426 | uint | RD | UTC timestamp: min. value, 54. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18428 | uint | RD | UTC timestamp: min. value, 55. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18430 | uint | RD | UTC timestamp: min. value, 56. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18432 | uint | RD | UTC timestamp: min. value, 57. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18434 | uint | RD | UTC timestamp: min. value, 58. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18436 | uint | RD | UTC timestamp: min. value, 59. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18438 | uint | RD | UTC timestamp: min. value, 60. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18440 | uint | RD | UTC timestamp: min. value, 61. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18442 | uint | RD | UTC timestamp: min. value, 62. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18444 | uint | RD | UTC timestamp: min. value, 63. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18446 | uint | RD | UTC timestamp: min. value, 64. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18448 | uint | RD | UTC timestamp: min. value, 65. harmonic voltage L2 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18450 | uint | RD | UTC timestamp: min. value, 41. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18452 | uint | RD | UTC timestamp: min. value, 42. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18454 | uint | RD | UTC timestamp: min. value, 43. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18456 | uint | RD | UTC timestamp: min. value, 44. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18458 | uint | RD | UTC timestamp: min. value, 45. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18460 | uint | RD | UTC timestamp: min. value, 46. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18462 | uint | RD | UTC timestamp: min. value, 47. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18464 | uint | RD | UTC timestamp: min. value, 48. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18466 | uint | RD | UTC timestamp: min. value, 49. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18468 | uint | RD | UTC timestamp: min. value, 50. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18470 | uint | RD | UTC timestamp: min. value, 51. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18472 | uint | RD | UTC timestamp: min. value, 52. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18474 | uint | RD | UTC timestamp: min. value, 53. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18476 | uint | RD | UTC timestamp: min. value, 54. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18478 | uint | RD | UTC timestamp: min. value, 55. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18480 | uint | RD | UTC timestamp: min. value, 56. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18482 | uint | RD | UTC timestamp: min. value, 57. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18484 | uint | RD | UTC timestamp: min. value, 58. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18486 | uint | RD | UTC timestamp: min. value, 59. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18488 | uint | RD | UTC timestamp: min. value, 60. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18490 | uint | RD | UTC timestamp: min. value, 61. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18492 | uint | RD | UTC timestamp: min. value, 62. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18494 | uint | RD | UTC timestamp: min. value, 63. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18496 | uint | RD | UTC timestamp: min. value, 64. harmonic voltage L3 | s
Minimalwerte, Zeitstempel, erweiterte Fourieranalyse | 55 | 18498 | uint | RD | UTC timestamp: min. value, 65. harmonic voltage L3 | s
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17300 | float | RD | Mean value: 41. harmonic voltage L1 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17302 | float | RD | Mean value: 42. harmonic voltage L1 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17304 | float | RD | Max. value: 43. harmonic voltage L1 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17306 | float | RD | Max. value: 44. harmonic voltage L1 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17308 | float | RD | Max. value: 45. harmonic voltage L1 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17310 | float | RD | Max. value: 46. harmonic voltage L1 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17312 | float | RD | Max. value: 47. harmonic voltage L1 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17314 | float | RD | Max. value: 48. harmonic voltage L1 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17316 | float | RD | Max. value: 49. harmonic voltage L1 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17318 | float | RD | Max. value: 50. harmonic voltage L1 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17320 | float | RD | Max. value: 51. harmonic voltage L1 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17322 | float | RD | Max. value: 52. harmonic voltage L1 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17324 | float | RD | Max. value: 53. harmonic voltage L1 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17326 | float | RD | Max. value: 54. harmonic voltage L1 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17328 | float | RD | Max. value: 55. harmonic voltage L1 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17330 | float | RD | Max. value: 56. harmonic voltage L1 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17332 | float | RD | Max. value: 57. harmonic voltage L1 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17334 | float | RD | Max. value: 58. harmonic voltage L1 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17336 | float | RD | Max. value: 59. harmonic voltage L1 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17338 | float | RD | Max. value: 60. harmonic voltage L1 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17340 | float | RD | Max. value: 61. harmonic voltage L1 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17342 | float | RD | Max. value: 62. harmonic voltage L1 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17344 | float | RD | Max. value: 63. harmonic voltage L1 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17346 | float | RD | Max. value: 64. harmonic voltage L1 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17348 | float | RD | Max. value: 65. harmonic voltage L1 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17350 | float | RD | Mean value: 41. harmonic voltage L2 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17352 | float | RD | Mean value: 42. harmonic voltage L2 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17354 | float | RD | Mean value: 43. harmonic voltage L2 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17356 | float | RD | Mean value: 44. harmonic voltage L2 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17358 | float | RD | Mean value: 45. harmonic voltage L2 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17360 | float | RD | Mean value: 46. harmonic voltage L2 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17362 | float | RD | Mean value: 47. harmonic voltage L2 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17364 | float | RD | Mean value: 48. harmonic voltage L2 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17366 | float | RD | Mean value: 49. harmonic voltage L2 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17368 | float | RD | Mean value: 50. harmonic voltage L2 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17370 | float | RD | Mean value: 51. harmonic voltage L2 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17372 | float | RD | Mean value: 52. harmonic voltage L2 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17374 | float | RD | Mean value: 53. harmonic voltage L2 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17376 | float | RD | Mean value: 54. harmonic voltage L2 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17378 | float | RD | Mean value: 55. harmonic voltage L2 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17380 | float | RD | Mean value: 56. harmonic voltage L2 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17382 | float | RD | Mean value: 57. harmonic voltage L2 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17384 | float | RD | Mean value: 58. harmonic voltage L2 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17386 | float | RD | Mean value: 59. harmonic voltage L2 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17388 | float | RD | Mean value: 60. harmonic voltage L2 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17390 | float | RD | Mean value: 61. harmonic voltage L2 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17392 | float | RD | Mean value: 62. harmonic voltage L2 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17394 | float | RD | Mean value: 63. harmonic voltage L2 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17396 | float | RD | Mean value: 64. harmonic voltage L2 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17398 | float | RD | Mean value: 65. harmonic voltage L2 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17400 | float | RD | Mean value: 41. harmonic voltage L3 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17402 | float | RD | Mean value: 42. harmonic voltage L3 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17404 | float | RD | Mean value: 43. harmonic voltage L3 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17406 | float | RD | Mean value: 44. harmonic voltage L3 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17408 | float | RD | Mean value: 45. harmonic voltage L3 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17410 | float | RD | Mean value: 46. harmonic voltage L3 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17412 | float | RD | Mean value: 47. harmonic voltage L3 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17414 | float | RD | Mean value: 48. harmonic voltage L3 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17416 | float | RD | Mean value: 49. harmonic voltage L3 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17418 | float | RD | Mean value: 50. harmonic voltage L3 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17420 | float | RD | Mean value: 51. harmonic voltage L3 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17422 | float | RD | Mean value: 52. harmonic voltage L3 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17424 | float | RD | Mean value: 53. harmonic voltage L3 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17426 | float | RD | Mean value: 54. harmonic voltage L3 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17428 | float | RD | Mean value: 55. harmonic voltage L3 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17430 | float | RD | Mean value: 56. harmonic voltage L3 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17432 | float | RD | Mean value: 57. harmonic voltage L3 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17434 | float | RD | Mean value: 58. harmonic voltage L3 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17436 | float | RD | Mean value: 59. harmonic voltage L3 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17438 | float | RD | Mean value: 60. harmonic voltage L3 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17440 | float | RD | Mean value: 61. harmonic voltage L3 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17442 | float | RD | Mean value: 62. harmonic voltage L3 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17444 | float | RD | Mean value: 63. harmonic voltage L3 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17446 | float | RD | Mean value: 64. harmonic voltage L3 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17448 | float | RD | Mean value: 65. harmonic voltage L3 | V
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17450 | float | RD | Mean value: 41. harmonic current L1 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17452 | float | RD | Mean value: 42. harmonic current L1 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17454 | float | RD | Mean value: 43. harmonic current L1 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17456 | float | RD | Mean value: 44. harmonic current L1 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17458 | float | RD | Mean value: 45. harmonic current L1 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17460 | float | RD | Mean value: 46. harmonic current L1 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17462 | float | RD | Mean value: 47. harmonic current L1 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17464 | float | RD | Mean value: 48. harmonic current L1 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17466 | float | RD | Mean value: 49. harmonic current L1 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17468 | float | RD | Mean value: 50. harmonic current L1 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17470 | float | RD | Mean value: 51. harmonic current L1 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17472 | float | RD | Mean value: 52. harmonic current L1 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17474 | float | RD | Mean value: 53. harmonic current L1 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17476 | float | RD | Mean value: 54. harmonic current L1 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17478 | float | RD | Mean value: 55. harmonic current L1 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17480 | float | RD | Mean value: 56. harmonic current L1 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17482 | float | RD | Mean value: 57. harmonic current L1 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17484 | float | RD | Mean value: 58. harmonic current L1 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17486 | float | RD | Mean value: 59. harmonic current L1 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17488 | float | RD | Mean value: 60. harmonic current L1 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17490 | float | RD | Mean value: 61. harmonic current L1 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17492 | float | RD | Mean value: 62. harmonic current L1 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17494 | float | RD | Mean value: 63. harmonic current L1 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17496 | float | RD | Mean value: 64. harmonic current L1 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17498 | float | RD | Mean value: 65. harmonic current L1 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17500 | float | RD | Mean value: 41. harmonic current L2 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17502 | float | RD | Mean value: 42. harmonic current L2 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17504 | float | RD | Mean value: 43. harmonic current L2 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17506 | float | RD | Mean value: 44. harmonic current L2 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17508 | float | RD | Mean value: 45. harmonic current L2 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17510 | float | RD | Mean value: 46. harmonic current L2 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17512 | float | RD | Mean value: 47. harmonic current L2 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17514 | float | RD | Mean value: 48. harmonic current L2 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17516 | float | RD | Mean value: 49. harmonic current L2 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17518 | float | RD | Mean value: 50. harmonic current L2 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17520 | float | RD | Mean value: 51. harmonic current L2 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17522 | float | RD | Mean value: 52. harmonic current L2 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17524 | float | RD | Mean value: 53. harmonic current L2 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17526 | float | RD | Mean value: 54. harmonic current L2 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17528 | float | RD | Mean value: 55. harmonic current L2 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17530 | float | RD | Mean value: 56. harmonic current L2 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17532 | float | RD | Mean value: 57. harmonic current L2 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17534 | float | RD | Mean value: 58. harmonic current L2 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17536 | float | RD | Mean value: 59. harmonic current L2 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17538 | float | RD | Mean value: 60. harmonic current L2 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17540 | float | RD | Mean value: 61. harmonic current L2 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17542 | float | RD | Mean value: 62. harmonic current L2 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17544 | float | RD | Mean value: 63. harmonic current L2 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17546 | float | RD | Mean value: 64. harmonic current L2 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17548 | float | RD | Mean value: 65. harmonic current L2 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17550 | float | RD | Mean value: 41. harmonic current L3 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17552 | float | RD | Mean value: 42. harmonic current L3 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17554 | float | RD | Mean value: 43. harmonic current L3 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17556 | float | RD | Mean value: 44. harmonic current L3 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17558 | float | RD | Mean value: 45. harmonic current L3 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17560 | float | RD | Mean value: 46. harmonic current L3 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17562 | float | RD | Mean value: 47. harmonic current L3 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17564 | float | RD | Mean value: 48. harmonic current L3 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17566 | float | RD | Mean value: 49. harmonic current L3 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17568 | float | RD | Mean value: 50. harmonic current L3 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17570 | float | RD | Mean value: 51. harmonic current L3 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17572 | float | RD | Mean value: 52. harmonic current L3 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17574 | float | RD | Mean value: 53. harmonic current L3 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17576 | float | RD | Mean value: 54. harmonic current L3 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17578 | float | RD | Mean value: 55. harmonic current L3 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17580 | float | RD | Mean value: 56. harmonic current L3 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17582 | float | RD | Mean value: 57. harmonic current L3 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17584 | float | RD | Mean value: 58. harmonic current L3 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17586 | float | RD | Mean value: 59. harmonic current L3 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17588 | float | RD | Mean value: 60. harmonic current L3 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17590 | float | RD | Mean value: 61. harmonic current L3 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17592 | float | RD | Mean value: 62. harmonic current L3 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17594 | float | RD | Mean value: 63. harmonic current L3 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17596 | float | RD | Mean value: 64. harmonic current L3 | A
Gleitende Mittelwerte, erweiterte Fourieranalyse | 56 | 17598 | float | RD | Mean value: 65. harmonic current L3 | A
Sonstige Parameter | 60 | 8 | char | RD/WR | Reset Min/Max values, 1 = Reset
Sonstige Parameter | 60 | 9 | char | RD/WR | Reset Energy values, 1 = Reset
Sonstige Parameter | 60 | 100 | uint | RD/WR | UTC timestamp for time synchronisation via Modbus (RS485)
Sonstige Parameter | 60 | 911 | uint | RD | Serial number
Sonstige Parameter | 60 | 20004 | ushort | RD | Firmeware version of the device. Example: '355' means version 3.55
Sonstige Parameter | 60 | 20012 | uint | RD/WR | Production number
Sonstige Parameter | 60 | 20016 | uint | RD/WR | Article number
Sonstige Parameter | 60 | 20047 | ushort | RD/WR | Device type ID: UMG 96-PA=19, UMG 96-PA-MID+=30, UMG 96-PQ-L=32, UMG 96-PQ-L (IT)=34, UMG 96-PQ-L-LP=38 |  | 0 | 65535
Sonstige Parameter | 60 | 25000 | string | RD/WR | freely programmable device name. Up to 127 characters
Sonstige Parameter | 60 | 25128 | string | RD/WR | Device description. Up to 239 characters
Sonstige Parameter | 60 | 31498 | ushort | RD/WR | clock synchronisation validation Interval in hours, set to zero to deactivate | h | 0 | 168
Sonstige Parameter | 60 | 31499 | ushort | RD | Validate time synchronization, 0 = valid
Sonstige Parameter | 60 | 31500 | ushort | RD/WR | EN60870 Time structure, Millisecond
Sonstige Parameter | 60 | 31501 | ushort | RD/WR | EN60870 Time structure, Minutes & Hour
Sonstige Parameter | 60 | 31502 | ushort | RD/WR | EN60870 Time structure, Day, Weekday & Month
Sonstige Parameter | 60 | 31503 | ushort | RD/WR | EN60870 Time structure, Year
Sonstige Parameter | 60 | 32604 | short | RD/WR | enable Modbus Broadcast, device will receive messages with slave address 0, 1 = enable |  | 0 | 1
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21000 | float | RD | 1. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21002 | float | RD | 2. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21004 | float | RD | 3. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21006 | float | RD | 4. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21008 | float | RD | 5. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21010 | float | RD | 6. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21012 | float | RD | 7. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21014 | float | RD | 8. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21016 | float | RD | 9. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21018 | float | RD | 10. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21020 | float | RD | 11. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21022 | float | RD | 12. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21024 | float | RD | 13. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21026 | float | RD | 14. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21028 | float | RD | 15. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21030 | float | RD | 16. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21032 | float | RD | 17. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21034 | float | RD | 18. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21036 | float | RD | 19. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21038 | float | RD | 20. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21040 | float | RD | 21. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21042 | float | RD | 22. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21044 | float | RD | 23. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21046 | float | RD | 24. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21048 | float | RD | 25. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21050 | float | RD | 26. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21052 | float | RD | 27. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21054 | float | RD | 28. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21056 | float | RD | 29. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21058 | float | RD | 30. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21060 | float | RD | 31. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21062 | float | RD | 32. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21064 | float | RD | 33. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21066 | float | RD | 34. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21068 | float | RD | 35. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21070 | float | RD | 36. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21072 | float | RD | 37. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21074 | float | RD | 38. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21076 | float | RD | 39. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21078 | float | RD | 40. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21080 | float | RD | 41. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21082 | float | RD | 42. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21084 | float | RD | 43. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21086 | float | RD | 44. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21088 | float | RD | 45. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21090 | float | RD | 46. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21092 | float | RD | 47. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21094 | float | RD | 48. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21096 | float | RD | 49. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21098 | float | RD | 50. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21100 | float | RD | 51. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21102 | float | RD | 52. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21104 | float | RD | 53. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21106 | float | RD | 54. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21108 | float | RD | 55. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21110 | float | RD | 56. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21112 | float | RD | 57. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21114 | float | RD | 58. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21116 | float | RD | 59. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21118 | float | RD | 60. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21120 | float | RD | 61. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21122 | float | RD | 62. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21124 | float | RD | 63. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21126 | float | RD | 64. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21128 | float | RD | 65. Interharmonics I-L1 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21130 | float | RD | 1. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21132 | float | RD | 2. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21134 | float | RD | 3. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21136 | float | RD | 4. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21138 | float | RD | 5. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21140 | float | RD | 6. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21142 | float | RD | 7. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21144 | float | RD | 8. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21146 | float | RD | 9. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21148 | float | RD | 10. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21150 | float | RD | 11. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21152 | float | RD | 12. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21154 | float | RD | 13. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21156 | float | RD | 14. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21158 | float | RD | 15. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21160 | float | RD | 16. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21162 | float | RD | 17. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21164 | float | RD | 18. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21166 | float | RD | 19. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21168 | float | RD | 20. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21170 | float | RD | 21. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21172 | float | RD | 22. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21174 | float | RD | 23. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21176 | float | RD | 24. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21178 | float | RD | 25. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21180 | float | RD | 26. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21182 | float | RD | 27. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21184 | float | RD | 28. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21186 | float | RD | 29. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21188 | float | RD | 30. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21190 | float | RD | 31. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21192 | float | RD | 32. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21194 | float | RD | 33. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21196 | float | RD | 34. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21198 | float | RD | 35. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21200 | float | RD | 36. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21202 | float | RD | 37. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21204 | float | RD | 38. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21206 | float | RD | 39. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21208 | float | RD | 40. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21210 | float | RD | 41. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21212 | float | RD | 42. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21214 | float | RD | 43. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21216 | float | RD | 44. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21218 | float | RD | 45. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21220 | float | RD | 46. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21222 | float | RD | 47. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21224 | float | RD | 48. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21226 | float | RD | 49. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21228 | float | RD | 50. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21230 | float | RD | 51. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21232 | float | RD | 52. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21234 | float | RD | 53. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21236 | float | RD | 54. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21238 | float | RD | 55. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21240 | float | RD | 56. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21242 | float | RD | 57. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21244 | float | RD | 58. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21246 | float | RD | 59. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21248 | float | RD | 60. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21250 | float | RD | 61. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21252 | float | RD | 62. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21254 | float | RD | 63. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21256 | float | RD | 64. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21258 | float | RD | 65. Interharmonics U-L1 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21260 | float | RD | 1. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21262 | float | RD | 2. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21264 | float | RD | 3. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21266 | float | RD | 4. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21268 | float | RD | 5. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21270 | float | RD | 6. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21272 | float | RD | 7. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21274 | float | RD | 8. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21276 | float | RD | 9. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21278 | float | RD | 10. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21280 | float | RD | 11. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21282 | float | RD | 12. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21284 | float | RD | 13. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21286 | float | RD | 14. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21288 | float | RD | 15. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21290 | float | RD | 16. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21292 | float | RD | 17. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21294 | float | RD | 18. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21296 | float | RD | 19. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21298 | float | RD | 20. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21300 | float | RD | 21. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21302 | float | RD | 22. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21304 | float | RD | 23. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21306 | float | RD | 24. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21308 | float | RD | 25. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21310 | float | RD | 26. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21312 | float | RD | 27. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21314 | float | RD | 28. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21316 | float | RD | 29. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21318 | float | RD | 30. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21320 | float | RD | 31. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21322 | float | RD | 32. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21324 | float | RD | 33. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21326 | float | RD | 34. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21328 | float | RD | 35. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21330 | float | RD | 36. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21332 | float | RD | 37. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21334 | float | RD | 38. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21336 | float | RD | 39. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21338 | float | RD | 40. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21340 | float | RD | 41. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21342 | float | RD | 42. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21344 | float | RD | 43. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21346 | float | RD | 44. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21348 | float | RD | 45. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21350 | float | RD | 46. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21352 | float | RD | 47. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21354 | float | RD | 48. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21356 | float | RD | 49. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21358 | float | RD | 50. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21360 | float | RD | 51. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21362 | float | RD | 52. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21364 | float | RD | 53. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21366 | float | RD | 54. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21368 | float | RD | 55. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21370 | float | RD | 56. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21372 | float | RD | 57. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21374 | float | RD | 58. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21376 | float | RD | 59. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21378 | float | RD | 60. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21380 | float | RD | 61. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21382 | float | RD | 62. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21384 | float | RD | 63. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21386 | float | RD | 64. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21388 | float | RD | 65. Interharmonics I-L2 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21390 | float | RD | 1. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21392 | float | RD | 2. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21394 | float | RD | 3. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21396 | float | RD | 4. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21398 | float | RD | 5. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21400 | float | RD | 6. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21402 | float | RD | 7. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21404 | float | RD | 8. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21406 | float | RD | 9. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21408 | float | RD | 10. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21410 | float | RD | 11. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21412 | float | RD | 12. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21414 | float | RD | 13. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21416 | float | RD | 14. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21418 | float | RD | 15. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21420 | float | RD | 16. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21422 | float | RD | 17. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21424 | float | RD | 18. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21426 | float | RD | 19. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21428 | float | RD | 20. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21430 | float | RD | 21. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21432 | float | RD | 22. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21434 | float | RD | 23. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21436 | float | RD | 24. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21438 | float | RD | 25. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21440 | float | RD | 26. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21442 | float | RD | 27. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21444 | float | RD | 28. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21446 | float | RD | 29. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21448 | float | RD | 30. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21450 | float | RD | 31. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21452 | float | RD | 32. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21454 | float | RD | 33. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21456 | float | RD | 34. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21458 | float | RD | 35. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21460 | float | RD | 36. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21462 | float | RD | 37. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21464 | float | RD | 38. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21466 | float | RD | 39. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21468 | float | RD | 40. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21470 | float | RD | 41. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21472 | float | RD | 42. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21474 | float | RD | 43. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21476 | float | RD | 44. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21478 | float | RD | 45. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21480 | float | RD | 46. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21482 | float | RD | 47. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21484 | float | RD | 48. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21486 | float | RD | 49. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21488 | float | RD | 50. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21490 | float | RD | 51. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21492 | float | RD | 52. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21494 | float | RD | 53. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21496 | float | RD | 54. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21498 | float | RD | 55. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21500 | float | RD | 56. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21502 | float | RD | 57. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21504 | float | RD | 58. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21506 | float | RD | 59. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21508 | float | RD | 60. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21510 | float | RD | 61. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21512 | float | RD | 62. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21514 | float | RD | 63. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21516 | float | RD | 64. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21518 | float | RD | 65. Interharmonics U-L2 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21520 | float | RD | 1. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21522 | float | RD | 2. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21524 | float | RD | 3. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21526 | float | RD | 4. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21528 | float | RD | 5. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21530 | float | RD | 6. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21532 | float | RD | 7. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21534 | float | RD | 8. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21536 | float | RD | 9. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21538 | float | RD | 10. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21540 | float | RD | 11. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21542 | float | RD | 12. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21544 | float | RD | 13. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21546 | float | RD | 14. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21548 | float | RD | 15. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21550 | float | RD | 16. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21552 | float | RD | 17. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21554 | float | RD | 18. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21556 | float | RD | 19. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21558 | float | RD | 20. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21560 | float | RD | 21. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21562 | float | RD | 22. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21564 | float | RD | 23. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21566 | float | RD | 24. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21568 | float | RD | 25. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21570 | float | RD | 26. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21572 | float | RD | 27. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21574 | float | RD | 28. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21576 | float | RD | 29. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21578 | float | RD | 30. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21580 | float | RD | 31. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21582 | float | RD | 32. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21584 | float | RD | 33. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21586 | float | RD | 34. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21588 | float | RD | 35. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21590 | float | RD | 36. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21592 | float | RD | 37. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21594 | float | RD | 38. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21596 | float | RD | 39. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21598 | float | RD | 40. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21600 | float | RD | 41. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21602 | float | RD | 42. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21604 | float | RD | 43. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21606 | float | RD | 44. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21608 | float | RD | 45. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21610 | float | RD | 46. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21612 | float | RD | 47. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21614 | float | RD | 48. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21616 | float | RD | 49. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21618 | float | RD | 50. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21620 | float | RD | 51. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21622 | float | RD | 52. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21624 | float | RD | 53. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21626 | float | RD | 54. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21628 | float | RD | 55. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21630 | float | RD | 56. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21632 | float | RD | 57. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21634 | float | RD | 58. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21636 | float | RD | 59. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21638 | float | RD | 60. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21640 | float | RD | 61. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21642 | float | RD | 62. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21644 | float | RD | 63. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21646 | float | RD | 64. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21648 | float | RD | 65. Interharmonics I-L3 | A
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21650 | float | RD | 1. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21652 | float | RD | 2. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21654 | float | RD | 3. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21656 | float | RD | 4. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21658 | float | RD | 5. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21660 | float | RD | 6. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21662 | float | RD | 7. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21664 | float | RD | 8. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21666 | float | RD | 9. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21668 | float | RD | 10. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21670 | float | RD | 11. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21672 | float | RD | 12. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21674 | float | RD | 13. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21676 | float | RD | 14. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21678 | float | RD | 15. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21680 | float | RD | 16. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21682 | float | RD | 17. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21684 | float | RD | 18. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21686 | float | RD | 19. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21688 | float | RD | 20. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21690 | float | RD | 21. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21692 | float | RD | 22. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21694 | float | RD | 23. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21696 | float | RD | 24. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21698 | float | RD | 25. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21700 | float | RD | 26. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21702 | float | RD | 27. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21704 | float | RD | 28. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21706 | float | RD | 29. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21708 | float | RD | 30. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21710 | float | RD | 31. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21712 | float | RD | 32. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21714 | float | RD | 33. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21716 | float | RD | 34. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21718 | float | RD | 35. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21720 | float | RD | 36. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21722 | float | RD | 37. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21724 | float | RD | 38. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21726 | float | RD | 39. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21728 | float | RD | 40. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21730 | float | RD | 41. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21732 | float | RD | 42. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21734 | float | RD | 43. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21736 | float | RD | 44. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21738 | float | RD | 45. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21740 | float | RD | 46. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21742 | float | RD | 47. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21744 | float | RD | 48. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21746 | float | RD | 49. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21748 | float | RD | 50. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21750 | float | RD | 51. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21752 | float | RD | 52. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21754 | float | RD | 53. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21756 | float | RD | 54. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21758 | float | RD | 55. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21760 | float | RD | 56. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21762 | float | RD | 57. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21764 | float | RD | 58. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21766 | float | RD | 59. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21768 | float | RD | 60. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21770 | float | RD | 61. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21772 | float | RD | 62. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21774 | float | RD | 63. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21776 | float | RD | 64. Interharmonics U-L3 | V
Zwischenharmonische - nur mit IEC 61000-4-30, Klasse S | 61 | 21778 | float | RD | 65. Interharmonics U-L3 | V
Flicker-Messwerte - nur mit IEC 61000-4-30, Klasse S | 62 | 1302 | short | RD/WR | Flicker system (50/60 Hz): 0 = 230V/50Hz, 1 = 120V/50Hz, 2 = 230V/60Hz, 3 = 120V/60Hz |  | 0 | 3
Flicker-Messwerte - nur mit IEC 61000-4-30, Klasse S | 62 | 1303 | float | RD | L1 Flicker long therm (2 h)
Flicker-Messwerte - nur mit IEC 61000-4-30, Klasse S | 62 | 1305 | float | RD | L2 Flicker long therm (2 h)
Flicker-Messwerte - nur mit IEC 61000-4-30, Klasse S | 62 | 1307 | float | RD | L3 Flicker long therm (2 h)
Flicker-Messwerte - nur mit IEC 61000-4-30, Klasse S | 62 | 1309 | float | RD | L1 Flicker short therm (10 min)
Flicker-Messwerte - nur mit IEC 61000-4-30, Klasse S | 62 | 1311 | float | RD | L2 Flicker short therm (10 min)
Flicker-Messwerte - nur mit IEC 61000-4-30, Klasse S | 62 | 1313 | float | RD | L3 Flicker short therm (10 min)
Flicker-Messwerte - nur mit IEC 61000-4-30, Klasse S | 62 | 1315 | float | RD | L1 Flicker perception factor
Flicker-Messwerte - nur mit IEC 61000-4-30, Klasse S | 62 | 1317 | float | RD | L2 Flicker perception factor
Flicker-Messwerte - nur mit IEC 61000-4-30, Klasse S | 62 | 1319 | float | RD | L3 Flicker perception factor
Flicker-Messwerte - nur mit IEC 61000-4-30, Klasse S | 62 | 1321 | uint | RD | UTC Starttime of Flicker short term
Flicker-Messwerte - nur mit IEC 61000-4-30, Klasse S | 62 | 1323 | uint | RD | UTC Endtime of Flicker short term
Flicker-Messwerte - nur mit IEC 61000-4-30, Klasse S | 62 | 1325 | uint | RD | UTC Starttime of Flicker long term
Flicker-Messwerte - nur mit IEC 61000-4-30, Klasse S | 62 | 1327 | uint | RD | UTC Endtime of Flicker long term
Weitere Parameter - nur mit IEC 61000-4-30, Klasse S | 63 | 1333 | float | RD/WR | Configurable frequency in Hz (float) for ripple control |  | 0 | 3000
Weitere Parameter - nur mit IEC 61000-4-30, Klasse S | 63 | 1335 | float | RD | Measured value (float): RMS of ripple control signal UL1 | V
Weitere Parameter - nur mit IEC 61000-4-30, Klasse S | 63 | 1337 | float | RD | Measured value (float): RMS of ripple control signal UL2 | V
Weitere Parameter - nur mit IEC 61000-4-30, Klasse S | 63 | 1339 | float | RD | Measured value (float): RMS of ripple control signal UL3 | V
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20053 | float | RD/WR | Measured value, current L4 | A | -3.403 e+38 | 3.403 e+38
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20063 | float | RD/WR | 1. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20065 | float | RD/WR | 2. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20067 | float | RD/WR | 3. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20069 | float | RD/WR | 4. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20071 | float | RD/WR | 5. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20073 | float | RD/WR | 6. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20075 | float | RD/WR | 7. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20077 | float | RD/WR | 8. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20079 | float | RD/WR | 9. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20081 | float | RD/WR | 10. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20083 | float | RD/WR | 11. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20085 | float | RD/WR | 12. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20087 | float | RD/WR | 13. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20089 | float | RD/WR | 14. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20091 | float | RD/WR | 15. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20093 | float | RD/WR | 16. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20095 | float | RD/WR | 17. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20097 | float | RD/WR | 18. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20099 | float | RD/WR | 19. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20101 | float | RD/WR | 20. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20103 | float | RD/WR | 21. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20105 | float | RD/WR | 22. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20107 | float | RD/WR | 23. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20109 | float | RD/WR | 24. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20111 | float | RD/WR | 25. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20113 | float | RD/WR | 26. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20115 | float | RD/WR | 27. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20117 | float | RD/WR | 28. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20119 | float | RD/WR | 29. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20121 | float | RD/WR | 30. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20123 | float | RD/WR | 31. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20125 | float | RD/WR | 32. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20127 | float | RD/WR | 33. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20129 | float | RD/WR | 34. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20131 | float | RD/WR | 35. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20133 | float | RD/WR | 36. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20135 | float | RD/WR | 37. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20137 | float | RD/WR | 38. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20139 | float | RD/WR | 39. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20141 | float | RD/WR | 40. harmonic current L4 | A
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20305 | float | RD/WR | mean value, current L4 | A | 0 | 3.403 e+38
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20315 | float | RD/WR | min. value, current L4 | A | 0 | 3.403 e+38
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20325 | float | RD/WR | max. value, current L4 | A | 0 | 3.403 e+38
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20335 | uint | RD/WR | UTC timestamp, min. value, current L4 | s
UMG 96-PQ-L-LP erweiterte Adressen | 70 | 20345 | uint | RD/WR | UTC timestamp, max. value, current L4 | s
RCM-Modul: Messwerte, Typ Float | 90 | 20053 | float | RD/WR | Measured value, current L4 | A | -3.403 e+38 | 3.403 e+38
RCM-Modul: Messwerte, Typ Float | 90 | 20055 | float | RD/WR | RCM module: current RCM1 (I5) | A | -3.403 e+38 | 3.403 e+38
RCM-Modul: Messwerte, Typ Float | 90 | 20057 | float | RD/WR | RCM module: current RCM2 (I6) | A | -3.403 e+38 | 3.403 e+38
RCM-Modul: Messwerte, Typ Float | 90 | 20059 | float | RD/WR | RCM module: current RCM2 (I6 prop. U6) | V | -3.403 e+38 | 3.403 e+38
RCM-Modul: Messwerte, Typ Float | 90 | 20061 | float | RD/WR | RCM module: ext. temperature | GRAD_C | -3.403 e+38 | 3.403 e+38
RCM-Modul: Messwerte, Typ Float | 90 | 20303 | float | RD/WR | RCM module: DC power (P=I5*U6) | W | 0 | 3.403 e+38
RCM-Modul: Gleitende Mittelwerte, Typ Float | 91 | 20305 | float | RD/WR | mean value, current L4 | A | 0 | 3.403 e+38
RCM-Modul: Gleitende Mittelwerte, Typ Float | 91 | 20307 | float | RD/WR | RCM module: mean value, current RCM1 (I5) | A | 0 | 3.403 e+38
RCM-Modul: Gleitende Mittelwerte, Typ Float | 91 | 20309 | float | RD/WR | RCM module: mean value, current RCM2 (I6) | A | 0 | 3.403 e+38
RCM-Modul: Gleitende Mittelwerte, Typ Float | 91 | 20311 | float | RD/WR | RCM module: mean value, current RCM2 (I6 prop. U6) | V | 0 | 3.403 e+38
RCM-Modul: Gleitende Mittelwerte, Typ Float | 91 | 20313 | float | RD/WR | RCM module: mean value, ext. temperature | GRAD_C | 0 | 3.403 e+38
RCM-Modul: Minimalwerte, Typ Float | 92 | 20315 | float | RD/WR | min. value, current L4 | A | 0 | 3.403 e+38
RCM-Modul: Minimalwerte, Typ Float | 92 | 20317 | float | RD/WR | RCM module: min. value, current RCM1 (I5) | A | 0 | 3.403 e+38
RCM-Modul: Minimalwerte, Typ Float | 92 | 20319 | float | RD/WR | RCM module: min. value, current RCM2 (I6) | A | 0 | 3.403 e+38
RCM-Modul: Minimalwerte, Typ Float | 92 | 20321 | float | RD/WR | RCM module: min. value, current RCM2 (I6 prop. U6) | V | 0 | 3.403 e+38
RCM-Modul: Minimalwerte, Typ Float | 92 | 20323 | float | RD/WR | RCM module: min. value, ext. temperature | GRAD_C | 0 | 3.403 e+38
RCM-Modul: Maximalwerte, Typ Float | 93 | 20325 | float | RD/WR | max. value, current L4 | A | 0 | 3.403 e+38
RCM-Modul: Maximalwerte, Typ Float | 93 | 20327 | float | RD/WR | RCM module: max. value, current RCM1 (I5) | A | 0 | 3.403 e+38
RCM-Modul: Maximalwerte, Typ Float | 93 | 20329 | float | RD/WR | RCM module: max. value, current RCM2 (I6) | A | 0 | 3.403 e+38
RCM-Modul: Maximalwerte, Typ Float | 93 | 20331 | float | RD/WR | RCM module: max. value, current RCM2 (I6 prop. U6) | V | 0 | 3.403 e+38
RCM-Modul: Maximalwerte, Typ Float | 93 | 20333 | float | RD/WR | RCM module: max. value, ext. temperature | GRAD_C | 0 | 3.403 e+38
RCM-Modul: Minimalwerte, Zeitstempel | 94 | 20335 | uint | RD/WR | UTC timestamp, min. value, current L4 | s
RCM-Modul: Minimalwerte, Zeitstempel | 94 | 20337 | uint | RD/WR | RCM module: UTC timestamp, min. value, current RCM1 (I5) | s
RCM-Modul: Minimalwerte, Zeitstempel | 94 | 20339 | uint | RD/WR | RCM module: UTC timestamp, min. value, current RCM2 (I6) | s
RCM-Modul: Minimalwerte, Zeitstempel | 94 | 20341 | uint | RD/WR | RCM module: UTC timestamp, min. value, current RCM2 (I6 prop. U6) | s
RCM-Modul: Minimalwerte, Zeitstempel | 94 | 20343 | uint | RD/WR | RCM module: UTC timestamp, min. value, ext. temperature | s
RCM-Modul: Maximalwerte, Zeitstempel | 95 | 20345 | uint | RD/WR | UTC timestamp, max. value, current L4 | s
RCM-Modul: Maximalwerte, Zeitstempel | 95 | 20347 | uint | RD/WR | RCM module: UTC timestamp, max. value, current RCM1 (I5) | s
RCM-Modul: Maximalwerte, Zeitstempel | 95 | 20349 | uint | RD/WR | RCM module: UTC timestamp, max. value, current RCM2 (I6) | s
RCM-Modul: Maximalwerte, Zeitstempel | 95 | 20351 | uint | RD/WR | RCM module: UTC timestamp, max. value, current RCM2 (I6 prop. U6) | s
RCM-Modul: Maximalwerte, Zeitstempel | 95 | 20353 | uint | RD/WR | RCM module: UTC timestamp, max. value, ext. temperature | s
RCM-Modul: Energiewerte | 96 | 20355 | double | RD/WR | RCM module: active energy, DC (I5 * U6) | Wh | 0 | 3.403 e+38
RCM-Modul: Energiewerte | 96 | 20359 | float | RD/WR | RCM module: active energy, DC (I5 * U6) | Wh | 0 | 3.403 e+38
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20063 | float | RD/WR | 1. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20065 | float | RD/WR | 2. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20067 | float | RD/WR | 3. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20069 | float | RD/WR | 4. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20071 | float | RD/WR | 5. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20073 | float | RD/WR | 6. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20075 | float | RD/WR | 7. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20077 | float | RD/WR | 8. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20079 | float | RD/WR | 9. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20081 | float | RD/WR | 10. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20083 | float | RD/WR | 11. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20085 | float | RD/WR | 12. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20087 | float | RD/WR | 13. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20089 | float | RD/WR | 14. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20091 | float | RD/WR | 15. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20093 | float | RD/WR | 16. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20095 | float | RD/WR | 17. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20097 | float | RD/WR | 18. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20099 | float | RD/WR | 19. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20101 | float | RD/WR | 20. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20103 | float | RD/WR | 21. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20105 | float | RD/WR | 22. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20107 | float | RD/WR | 23. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20109 | float | RD/WR | 24. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20111 | float | RD/WR | 25. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20113 | float | RD/WR | 26. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20115 | float | RD/WR | 27. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20117 | float | RD/WR | 28. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20119 | float | RD/WR | 29. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20121 | float | RD/WR | 30. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20123 | float | RD/WR | 31. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20125 | float | RD/WR | 32. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20127 | float | RD/WR | 33. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20129 | float | RD/WR | 34. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20131 | float | RD/WR | 35. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20133 | float | RD/WR | 36. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20135 | float | RD/WR | 37. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20137 | float | RD/WR | 38. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20139 | float | RD/WR | 39. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20141 | float | RD/WR | 40. harmonic current L4 | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20143 | float | RD/WR | RCM module: 1. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20145 | float | RD/WR | RCM module: 2. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20147 | float | RD/WR | RCM module: 3. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20149 | float | RD/WR | RCM module: 4. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20151 | float | RD/WR | RCM module: 5. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20153 | float | RD/WR | RCM module: 6. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20155 | float | RD/WR | RCM module: 7. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20157 | float | RD/WR | RCM module: 8. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20159 | float | RD/WR | RCM module: 9. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20161 | float | RD/WR | RCM module: 10. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20163 | float | RD/WR | RCM module: 11. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20165 | float | RD/WR | RCM module: 12. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20167 | float | RD/WR | RCM module: 13. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20169 | float | RD/WR | RCM module: 14. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20171 | float | RD/WR | RCM module: 15. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20173 | float | RD/WR | RCM module: 16. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20175 | float | RD/WR | RCM module: 17. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20177 | float | RD/WR | RCM module: 18. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20179 | float | RD/WR | RCM module: 19. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20181 | float | RD/WR | RCM module: 20. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20183 | float | RD/WR | RCM module: 21. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20185 | float | RD/WR | RCM module: 22. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20187 | float | RD/WR | RCM module: 23. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20189 | float | RD/WR | RCM module: 24. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20191 | float | RD/WR | RCM module: 25. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20193 | float | RD/WR | RCM module: 26. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20195 | float | RD/WR | RCM module: 27. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20197 | float | RD/WR | RCM module: 28. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20199 | float | RD/WR | RCM module: 29. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20201 | float | RD/WR | RCM module: 30. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20203 | float | RD/WR | RCM module: 31. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20205 | float | RD/WR | RCM module: 32. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20207 | float | RD/WR | RCM module: 33. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20209 | float | RD/WR | RCM module: 34. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20211 | float | RD/WR | RCM module: 35. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20213 | float | RD/WR | RCM module: 36. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20215 | float | RD/WR | RCM module: 37. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20217 | float | RD/WR | RCM module: 38. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20219 | float | RD/WR | RCM module: 39. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20221 | float | RD/WR | RCM module: 40. harmonic current rcm1 (I5) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20223 | float | RD/WR | RCM module: 1. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20225 | float | RD/WR | RCM module: 2. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20227 | float | RD/WR | RCM module: 3. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20229 | float | RD/WR | RCM module: 4. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20231 | float | RD/WR | RCM module: 5. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20233 | float | RD/WR | RCM module: 6. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20235 | float | RD/WR | RCM module: 7. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20237 | float | RD/WR | RCM module: 8. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20239 | float | RD/WR | RCM module: 9. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20241 | float | RD/WR | RCM module: 10. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20243 | float | RD/WR | RCM module: 11. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20245 | float | RD/WR | RCM module: 12. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20247 | float | RD/WR | RCM module: 13. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20249 | float | RD/WR | RCM module: 14. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20251 | float | RD/WR | RCM module: 15. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20253 | float | RD/WR | RCM module: 16. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20255 | float | RD/WR | RCM module: 17. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20257 | float | RD/WR | RCM module: 18. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20259 | float | RD/WR | RCM module: 19. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20261 | float | RD/WR | RCM module: 20. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20263 | float | RD/WR | RCM module: 21. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20265 | float | RD/WR | RCM module: 22. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20267 | float | RD/WR | RCM module: 23. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20269 | float | RD/WR | RCM module: 24. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20271 | float | RD/WR | RCM module: 25. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20273 | float | RD/WR | RCM module: 26. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20275 | float | RD/WR | RCM module: 27. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20277 | float | RD/WR | RCM module: 28. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20279 | float | RD/WR | RCM module: 29. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20281 | float | RD/WR | RCM module: 30. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20283 | float | RD/WR | RCM module: 31. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20285 | float | RD/WR | RCM module: 32. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20287 | float | RD/WR | RCM module: 33. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20289 | float | RD/WR | RCM module: 34. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20291 | float | RD/WR | RCM module: 35. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20293 | float | RD/WR | RCM module: 36. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20295 | float | RD/WR | RCM module: 37. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20297 | float | RD/WR | RCM module: 38. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20299 | float | RD/WR | RCM module: 39. harmonic current rcm2 (I6) | A
RCM-Modul: Fourieranalyse, Messwerte, Float | 98 | 20301 | float | RD/WR | RCM module: 40. harmonic current rcm2 (I6) | A
RCM-Modul: Sonstige Parameter | 99 | 196 | ushort | RD/WR | Firmeware version of the module. Example: '215' means version 2.15
RCM-Modul: Sonstige Parameter | 99 | 20051 | ushort | RD/WR | RCM module: RCM1 (I5): CT connection monitoring (AC only): 0=disable; 1=enable |  | 0 | 1
RCM-Modul: Sonstige Parameter | 99 | 20052 | ushort | RD/WR | RCM module: RCM2 (I6): CT connection monitoring (AC only): 0=disable; 1=enable |  | 0 | 1
RCM-Modul: Sonstige Parameter | 99 | 20393 | ushort | RD | RCM module: RCM1 (I5): status overcurrent, currently: 0= not available; 1= available
RCM-Modul: Sonstige Parameter | 99 | 20394 | ushort | RD/WR | RCM module: RCM1 (I5): status overcurrent, previously: 0= not available; 1= available
RCM-Modul: Sonstige Parameter | 99 | 20395 | ushort | RD | RCM module: RCM1 (I5): status rcm: Bit 0=1 warning currently available, Bit 1=1 warning previously available, Bit 2=1 alarm currently available, Bit 3=1: alarm previously available, Bit 4=1: CT connection break currently available, Bit 5=1: CT connection break previously available, Bit 6=1: overcurrent currently available, Bit 7=1: overcurrent previously available
RCM-Modul: Sonstige Parameter | 99 | 20396 | float | RD | RCM module: RCM1 (I5): current limit (in A) for alarms
RCM-Modul: Sonstige Parameter | 99 | 20398 | uint | RD | RCM module: RCM1 (I5): alarm run time (in ms)
RCM-Modul: Sonstige Parameter | 99 | 20413 | ushort | RD/WR | RCM module: RCM1 (I5): status overcurrent: Bit 0=1 warning currently available, Bit 1=1 warning previously available, Bit 2=1 alarm currently available, Bit 3=1: alarm previously available, Bit 4=1: CT connection break currently available, Bit 5=1: CT connection break previously available, Bit 6=1: overcurrent currently available, Bit 7=1: overcurrent previously available
RCM-Modul: Sonstige Parameter | 99 | 20414 | ushort | RD | RCM module: RCM1 (I5): status (pre-)warning, currently: 0=no warning available; 1=warning available
RCM-Modul: Sonstige Parameter | 99 | 20415 | ushort | RD/WR | RCM module: RCM1 (I5): status (pre-)warning, previously: 0=no warning available/delete alarm; 1=warning available
RCM-Modul: Sonstige Parameter | 99 | 20416 | ushort | RD | RCM module: RCM1 (I5): status alarm, currently: 0=no warning available; 1=warning available
RCM-Modul: Sonstige Parameter | 99 | 20417 | ushort | RD/WR | RCM module: RCM1 (I5): status alarm, previously: 0=no warning available/delete alarm; 1=warning available
RCM-Modul: Sonstige Parameter | 99 | 20418 | ushort | RD | RCM module: RCM1 (I5): CT connections (AC only), currently: 0=error-free; 1=error
RCM-Modul: Sonstige Parameter | 99 | 20419 | ushort | RD/WR | RCM module: RCM1 (I5): CT connections (AC only), previously: 0=error-free/delete error; 1=error
RCM-Modul: Sonstige Parameter | 99 | 20593 | ushort | RD | RCM module: RCM2 (I6): status overcurrent, currently: 0= not available; 1= available
RCM-Modul: Sonstige Parameter | 99 | 20594 | ushort | RD/WR | RCM module: RCM2 (I6): status overcurrent, previously: 0= not available; 1= available
RCM-Modul: Sonstige Parameter | 99 | 20595 | ushort | RD | RCM module: RCM2 (I6): status: Bit 0=1 warning currently available, Bit 1=1 warning previously available, Bit 2=1 alarm currently available, Bit 3=1: alarm previously available, Bit 4=1: CT connection break currently available, Bit 5=1: CT connection break previously available, Bit 6=1: overcurrent currently available, Bit 7=1: overcurrent previously available
RCM-Modul: Sonstige Parameter | 99 | 20596 | float | RD | RCM module: RCM2 (I6): current limit (in A) for alarms
RCM-Modul: Sonstige Parameter | 99 | 20598 | uint | RD | RCM module: RCM2 (I6): alarm run time (in ms)
RCM-Modul: Sonstige Parameter | 99 | 20613 | ushort | RD/WR | RCM module: RCM2 (I6): status overcurrent: Bit 0=1 warning currently available, Bit 1=1 warning previously available, Bit 2=1 alarm currently available, Bit 3=1: alarm previously available, Bit 4=1: CT connection break currently available, Bit 5=1: CT connection break previously available, Bit 6=1: overcurrent currently available, Bit 7=1: overcurrent previously available
RCM-Modul: Sonstige Parameter | 99 | 20614 | ushort | RD | RCM module: RCM2 (I6: status (pre-)warning, currently: 0=no alarm available; 1=alarm available
RCM-Modul: Sonstige Parameter | 99 | 20615 | ushort | RD/WR | RCM module: RCM2 (I6): status (pre-)warning, previously: 0=no warning available/delete alarm; 1=warning available
RCM-Modul: Sonstige Parameter | 99 | 20616 | ushort | RD | RCM module: RCM2 (I6): status alarm, currently: 0=no alarm available; 1=alarm available
RCM-Modul: Sonstige Parameter | 99 | 20617 | ushort | RD/WR | RCM module: RCM2 (I6): status alarm, previously: 0=no alarm available/delete alarm; 1=alarm available
RCM-Modul: Sonstige Parameter | 99 | 20618 | ushort | RD | RCM module: RCM2 (I6): CT connections (AC only), currently: 0=error-free; 1=error
RCM-Modul: Sonstige Parameter | 99 | 20619 | ushort | RD/WR | RCM module: RCM2 (I6): CT connections (AC only), previously: 0=error-free/delete error; 1=error
RCM-Modul: Sonstige Parameter | 99 | 20701 | ushort | RD | RCM module: Warning (3 days - not synchronized) - only MID+
RCM-Modul: Sonstige Parameter | 99 | 20702 | ushort | RD | RCM module: Alarm (7 days - not synchronized) - only MID+

## Sheet1(EN)
Category | Sort order (category) | Address | Type | Access Right | Description | Unit | Min | Max
Frequently required measured values | 1 | 19000 | float | RD | Voltage L1-N | V
Frequently required measured values | 1 | 19002 | float | RD | Voltage L2-N | V
Frequently required measured values | 1 | 19004 | float | RD | Voltage L3-N | V
Frequently required measured values | 1 | 19006 | float | RD | Voltage L1-L2 | V
Frequently required measured values | 1 | 19008 | float | RD | Voltage L2-L3 | V
Frequently required measured values | 1 | 19010 | float | RD | Voltage L3-L1 | V
Frequently required measured values | 1 | 19012 | float | RD | Current, L1 | A
Frequently required measured values | 1 | 19014 | float | RD | Current, L2 | A
Frequently required measured values | 1 | 19016 | float | RD | Current, L3 | A
Frequently required measured values | 1 | 19018 | float | RD | Vector sum, IN=I1+I2+I3 | A
Frequently required measured values | 1 | 19020 | float | RD | Real power L1 | W
Frequently required measured values | 1 | 19022 | float | RD | Real power L2 | W
Frequently required measured values | 1 | 19024 | float | RD | Real power L3 | W
Frequently required measured values | 1 | 19026 | float | RD | Sum, Psum3=P1+P2+P3 | W
Frequently required measured values | 1 | 19028 | float | RD | Apparent power L1 | VA
Frequently required measured values | 1 | 19030 | float | RD | Apparent power L2 | VA
Frequently required measured values | 1 | 19032 | float | RD | Apparent power L3 | VA
Frequently required measured values | 1 | 19034 | float | RD | Sum, Ssum3=S1+S2+S3 | VA
Frequently required measured values | 1 | 19036 | float | RD | Reactive power (mains frequ.) L1 | var
Frequently required measured values | 1 | 19038 | float | RD | Reactive power (mains frequ.) L2 | var
Frequently required measured values | 1 | 19040 | float | RD | Reactive power (mains frequ.) L3 | var
Frequently required measured values | 1 | 19042 | float | RD | Sum, Qsum3=Q1+Q2+Q3 | var
Frequently required measured values | 1 | 19044 | float | RD | Power factor fundamental oscill., Cos(ϕ), UL1 IL1
Frequently required measured values | 1 | 19046 | float | RD | Power factor fundamental oscill., Cos(ϕ),, UL2 IL2
Frequently required measured values | 1 | 19048 | float | RD | Power factor fundamental oscill., Cos(ϕ),, UL3 IL3
Frequently required measured values | 1 | 19050 | float | RD | Measured frequency | Hz
Frequently required measured values | 1 | 19052 | float | RD | Rotation field, 1=right, 0=none, -1=left
Frequently required measured values | 1 | 19054 | float | RD | Real energy L1, consumed | Wh
Frequently required measured values | 1 | 19056 | float | RD | Real energy L2, consumed | Wh
Frequently required measured values | 1 | 19058 | float | RD | Real energy L3, consumed | Wh
Frequently required measured values | 1 | 19060 | float | RD | Real energy L1..L3 | Wh
Frequently required measured values | 1 | 19062 | float | RD | Real energy L1, consumed | Wh
Frequently required measured values | 1 | 19064 | float | RD | Real energy L2, consumed | Wh
Frequently required measured values | 1 | 19066 | float | RD | Real energy L3, consumed | Wh
Frequently required measured values | 1 | 19068 | float | RD | Real energy L1..L3, consumed, rate 1 | Wh
Frequently required measured values | 1 | 19070 | float | RD | Real energy L1, delivered | Wh
Frequently required measured values | 1 | 19072 | float | RD | Real energy L2, delivered | Wh
Frequently required measured values | 1 | 19074 | float | RD | Real energy L3, delivered | Wh
Frequently required measured values | 1 | 19076 | float | RD | Real energy L1..L3, delivered | Wh
Frequently required measured values | 1 | 19078 | float | RD | Apparent energy L1 | VAh
Frequently required measured values | 1 | 19080 | float | RD | Apparent energy L2 | VAh
Frequently required measured values | 1 | 19082 | float | RD | Apparent energy L3 | VAh
Frequently required measured values | 1 | 19084 | float | RD | Apparent energy L1..L3 | VAh
Frequently required measured values | 1 | 19086 | float | RD | Reactive energy, inductive, L1 | varh
Frequently required measured values | 1 | 19088 | float | RD | Reactive energy, inductive, L2 | varh
Frequently required measured values | 1 | 19090 | float | RD | Reactive energy, inductive, L3 | varh
Frequently required measured values | 1 | 19092 | float | RD | Reactive energy L1..L3 | varh
Frequently required measured values | 1 | 19094 | float | RD | Reactive energy, inductive, L1 | varh
Frequently required measured values | 1 | 19096 | float | RD | Reactive energy, inductive, L2 | varh
Frequently required measured values | 1 | 19098 | float | RD | Reactive energy, inductive, L3 | varh
Frequently required measured values | 1 | 19100 | float | RD | Reactive energy L1..L3, ind. | varh
Frequently required measured values | 1 | 19102 | float | RD | Reactive energy, capacitive, L1 | varh
Frequently required measured values | 1 | 19104 | float | RD | Reactive energy, capacitive, L2 | varh
Frequently required measured values | 1 | 19106 | float | RD | Reactive energy, capacitive, L3 | varh
Frequently required measured values | 1 | 19108 | float | RD | Reactive energy L1..L3, cap. | varh
Frequently required measured values | 1 | 19110 | float | RD | Harmonic, THD,U L1-N | %
Frequently required measured values | 1 | 19112 | float | RD | Harmonic, THD,U L2-N | %
Frequently required measured values | 1 | 19114 | float | RD | Harmonic, THD,U L3-N | %
Frequently required measured values | 1 | 19116 | float | RD | Harmonic, THD,I L1 | %
Frequently required measured values | 1 | 19118 | float | RD | Harmonic, THD,I L2 | %
Frequently required measured values | 1 | 19120 | float | RD | Harmonic, THD,I L3 | %
Measured values | 2 | 991 | float | RD | Measured value (float): current max value for current RMS of all 3 phases | A
Measured values | 2 | 993 | ushort | RD | Measured value (float): the corresponding phase number (1...3)
Measured values | 2 | 1000 | float | RD | Measured value (float): voltage L1-N | V
Measured values | 2 | 1002 | float | RD | Measured value (float): voltage L2-N | V
Measured values | 2 | 1004 | float | RD | Measured value (float): voltage L3-N | V
Measured values | 2 | 1006 | float | RD | Measured value (float): voltage L1-L2 | V
Measured values | 2 | 1008 | float | RD | Measured value (float): voltage L2-L3 | V
Measured values | 2 | 1010 | float | RD | Measured value (float): voltage L3-L1 | V
Measured values | 2 | 1012 | float | RD | Measured value (float): current L1 | A
Measured values | 2 | 1014 | float | RD | Measured value (float): current L2 | A
Measured values | 2 | 1016 | float | RD | Measured value (float): current L3 | A
Measured values | 2 | 1018 | float | RD | Measured value (float): current sum (calculated current in N) | A
Measured values | 2 | 1020 | float | RD | Measured value (float): active power L1 | W
Measured values | 2 | 1022 | float | RD | Measured value (float): active power L2 | W
Measured values | 2 | 1024 | float | RD | Measured value (float): active power L3 | W
Measured values | 2 | 1026 | float | RD | Measured value (float): active power sum | W
Measured values | 2 | 1028 | float | RD | Measured value (float): reactive power L1 | var
Measured values | 2 | 1030 | float | RD | Measured value (float): reactive power L2 | var
Measured values | 2 | 1032 | float | RD | Measured value (float): reactive power L3 | var
Measured values | 2 | 1034 | float | RD | Measured value (float): reactive power sum | var
Measured values | 2 | 1036 | float | RD | Measured value (float): apparent power L1 | VA
Measured values | 2 | 1038 | float | RD | Measured value (float): apparent power L2 | VA
Measured values | 2 | 1040 | float | RD | Measured value (float): apparent power L3 | VA
Measured values | 2 | 1042 | float | RD | Measured value (float): apparent power sum | VA
Measured values | 2 | 1044 | float | RD | Measured value (float): cos(ϕ) L1
Measured values | 2 | 1046 | float | RD | Measured value (float): cos(ϕ) L2
Measured values | 2 | 1048 | float | RD | Measured value (float): cos(ϕ) L3
Measured values | 2 | 1050 | float | RD | Measured value (float): cos(ϕ) sum
Measured values | 2 | 1052 | float | RD | Measured value (float): active power of the fundamental oscillation L1 | W
Measured values | 2 | 1054 | float | RD | Measured value (float): active power of the fundamental oscillation L2 | W
Measured values | 2 | 1056 | float | RD | Measured value (float): active power of the fundamental oscillation L3 | W
Measured values | 2 | 1214 | float | RD | Measured value (float): THD voltage L1 [%] | %
Measured values | 2 | 1216 | float | RD | Measured value (float): THD voltage L2 [%] | %
Measured values | 2 | 1218 | float | RD | Measured value (float): THD voltage L3 [%] | %
Measured values | 2 | 1220 | float | RD | Measured value (float): THD current L1 [%] | %
Measured values | 2 | 1222 | float | RD | Measured value (float): THD current L1 [%] | %
Measured values | 2 | 1224 | float | RD | Measured value (float): THD current L1 [%] | %
Measured values | 2 | 1226 | float | RD | Measured value (float): frequency | Hz
Measured values | 2 | 1228 | float | RD | Measured value (float): zero sequence voltage
Measured values | 2 | 1230 | float | RD | Measured value (float): positive sequence voltage
Measured values | 2 | 1232 | float | RD | Measured value (float): negative sequence voltage
Measured values | 2 | 1234 | float | RD | Measured value (float): zero sequence current
Measured values | 2 | 1236 | float | RD | Measured value (float): positive sequence current
Measured values | 2 | 1238 | float | RD | Measured value (float): negative sequence current
Measured values | 2 | 1240 | float | RD | Measured value (float): distortion power L1 | var
Measured values | 2 | 1242 | float | RD | Measured value (float): distortion power L2 | var
Measured values | 2 | 1244 | float | RD | Measured value (float): distortion power L3 | var
Measured values | 2 | 1246 | float | RD | Measured value (float): distortion power sum | var
Measured values | 2 | 1248 | float | RD | Measured value (float): Rotation field, 1=right, 0=none, -1=left
Measured values | 2 | 1250 | float | RD | Measured value (float): real part of the fundamental oscillation voltage L1 | V
Measured values | 2 | 1252 | float | RD | Measured value (float): imaginary part of the fundamental oscillation voltage L1 | V
Measured values | 2 | 1254 | float | RD | Measured value (float): real part of the fundamental oscillation voltage L2 | V
Measured values | 2 | 1256 | float | RD | Measured value (float): imaginary part of the fundamental oscillation voltage L2 | V
Measured values | 2 | 1258 | float | RD | Measured value (float): real part of the fundamental oscillation voltage L3 | V
Measured values | 2 | 1260 | float | RD | Measured value (float): imaginary part of the fundamental oscillation voltage L3 | V
Measured values | 2 | 1262 | float | RD | Measured value (float): real part of the fundamental oscillation current L1 | A
Measured values | 2 | 1264 | float | RD | Measured value (float): imaginary part of the fundamental oscillation current L1 | A
Measured values | 2 | 1266 | float | RD | Measured value (float): real part of the fundamental oscillation current L2 | A
Measured values | 2 | 1268 | float | RD | Measured value (float): imaginary part of the fundamental oscillation current L2 | A
Measured values | 2 | 1270 | float | RD | Measured value (float): real part of the fundamental oscillation current L3 | A
Measured values | 2 | 1272 | float | RD | Measured value (float): imaginary part of the fundamental oscillation current L3 | A
Measured values | 2 | 1274 | float | RD | Measured value (float): frequency (200ms) | Hz
Measured values | 2 | 1276 | float | RD | Measured value (float): TDD (total demand distortion) current L1 | %
Measured values | 2 | 1278 | float | RD | Measured value (float): TDD (total demand distortion) current L2 | %
Measured values | 2 | 1280 | float | RD | Measured value (float): TDD (total demand distortion) current L3 | %
Measured values | 2 | 1282 | float | RD | Measured value (float): crest factor voltageL1
Measured values | 2 | 1284 | float | RD | Measured value (float): crest factor voltageL2
Measured values | 2 | 1286 | float | RD | Measured value (float): crest factor voltageL3
Measured values | 2 | 1288 | float | RD | Measured value (float): crest factor current L1
Measured values | 2 | 1290 | float | RD | Measured value (float): crest factor current L2
Measured values | 2 | 1292 | float | RD | Measured value (float): crest factor current L3
Measured values | 2 | 1294 | float | RD | Measured value (float): power factor L1
Measured values | 2 | 1296 | float | RD | Measured value (float): power factor L2
Measured values | 2 | 1298 | float | RD | Measured value (float): power factor L3
Measured values | 2 | 1300 | float | RD | Measured value (float): power factor sum3=Psum3/Ssum3
Measured values | 2 | 1329 | float | RD | Measured value (float): voltage asymmetry [%] | %
Measured values | 2 | 1331 | float | RD | Measured value (float): current asymmetry [%] | %
Measured values | 2 | 1400 | float | RD | Angular shift of the current I1 in the unit circle, relative to normal zero | deg
Measured values | 2 | 1402 | float | RD | Angular shift of the current I2 in the unit circle, relative to normal zero | deg
Measured values | 2 | 1404 | float | RD | Angular shift of the current I3 in the unit circle, relative to normal zero | deg
Measured values | 2 | 11000 | short (x10) | RD | Measured value (short): voltage L1-N | V
Measured values | 2 | 11001 | short (x10) | RD | Measured value (short): voltage L2-N | V
Measured values | 2 | 11002 | short (x10) | RD | Measured value (short): voltage L3-N | V
Measured values | 2 | 11003 | short (x10) | RD | Measured value (short): voltage L1-L2 | V
Measured values | 2 | 11004 | short (x10) | RD | Measured value (short): voltage L2-L3 | V
Measured values | 2 | 11005 | short (x10) | RD | Measured value (short): voltage L3-L1 | V
Measured values | 2 | 11006 | short (x1000) | RD | Measured value (short): current L1 | A
Measured values | 2 | 11007 | short (x1000) | RD | Measured value (short): current L2 | A
Measured values | 2 | 11008 | short (x1000) | RD | Measured value (short): current L3 | A
Measured values | 2 | 11009 | short (x1000) | RD | Measured value (short): current sum | A
Measured values | 2 | 11010 | short (x10) | RD | Measured value (short): active power L1 | W
Measured values | 2 | 11011 | short (x10) | RD | Measured value (short): active power L2 | W
Measured values | 2 | 11012 | short (x10) | RD | Measured value (short): active power L3 | W
Measured values | 2 | 11013 | short | RD | Measured value (short): active power sum | W
Measured values | 2 | 11014 | short (x10) | RD | Measured value (short): reactive power L1 | var
Measured values | 2 | 11015 | short (x10) | RD | Measured value (short): reactive power L2 | var
Measured values | 2 | 11016 | short (x10) | RD | Measured value (short): reactive power L3 | var
Measured values | 2 | 11017 | short | RD | Measured value (short): reactive power sum | var
Measured values | 2 | 11018 | short (x10) | RD | Measured value (short): apparent power L1 | VA
Measured values | 2 | 11019 | short (x10) | RD | Measured value (short): apparent power L2 | VA
Measured values | 2 | 11020 | short (x10) | RD | Measured value (short): apparent power L3 | VA
Measured values | 2 | 11021 | short | RD | Measured value (short): apparent power sum | VA
Measured values | 2 | 11022 | short (x100) | RD | Measured value (short): cos(ϕ) L1
Measured values | 2 | 11023 | short (x100) | RD | Measured value (short): cos(ϕ) L2
Measured values | 2 | 11024 | short (x100) | RD | Measured value (short): cos(ϕ) L3
Measured values | 2 | 11025 | short (x100) | RD | Measured value (short): cos(ϕ) sum
Measured values | 2 | 11026 | short (x10) | RD | Measured value (short): active power fundamental oscillation L1 | W
Measured values | 2 | 11027 | short (x10) | RD | Measured value (short): active power fundamental oscillation L2 | W
Measured values | 2 | 11028 | short (x10) | RD | Measured value (short): active power fundamental oscillation L3 | W
Measured values | 2 | 11111 | short (x100) | RD | Measured value (short): THD voltage L1-N [%] | %
Measured values | 2 | 11112 | short (x100) | RD | Measured value (short): THD voltage L2-N [%] | %
Measured values | 2 | 11113 | short (x100) | RD | Measured value (short): THD voltage L3-N [%] | %
Measured values | 2 | 11114 | short (x100) | RD | Measured value (short): THD current L1 [%] | %
Measured values | 2 | 11115 | short (x100) | RD | Measured value (short): THD current L2 [%] | %
Measured values | 2 | 11116 | short (x100) | RD | Measured value (short): THD current L3 [%] | %
Measured values | 2 | 11117 | short (x10) | RD | Measured value (short): frequency | Hz
Measured values | 2 | 11118 | short (x10) | RD | Measured value (short): zero sequence voltage
Measured values | 2 | 11119 | short (x10) | RD | Measured value (short): positive sequence voltage
Measured values | 2 | 11120 | short (x10) | RD | Measured value (short): negative sequence voltage
Measured values | 2 | 11121 | short (x1000) | RD | Measured value (short): zero sequence current
Measured values | 2 | 11122 | short (x1000) | RD | Measured value (short): positive sequence current
Measured values | 2 | 11123 | short (x1000) | RD | Measured value (short): negative sequence current
Measured values | 2 | 11124 | short (x10) | RD | Measured value (short): distortion power L1 | var
Measured values | 2 | 11125 | short (x10) | RD | Measured value (short): distortion power L2 | var
Measured values | 2 | 11126 | short (x10) | RD | Measured value (short): distortion power L3 | var
Measured values | 2 | 11127 | short | RD | Measured value (short): distortion power sum | var
Measured values | 2 | 11128 | short (x10) | RD | Measured value (short): Rotation field: > 0 = right, 0 = none, < 0 = left
Measured values | 2 | 11168 | ushort (x1000) | RD | Measured value (short): crest factor voltage L1-N
Measured values | 2 | 11169 | ushort (x1000) | RD | Measured value (short): crest factor voltage L2-N
Measured values | 2 | 11170 | ushort (x1000) | RD | Measured value (short): crest factor voltage L3-N
Measured values | 2 | 11171 | ushort (x1000) | RD | Measured value (short): crest factor current L1
Measured values | 2 | 11172 | ushort (x1000) | RD | Measured value (short): crest factor current L2
Measured values | 2 | 11173 | ushort (x1000) | RD | Measured value (short): crest factor current L3
Maximum values | 4 | 3000 | float | RD | Maximum value (float): voltage L1-N | V
Maximum values | 4 | 3002 | float | RD | Maximum value (float): voltage L2-N | V
Maximum values | 4 | 3004 | float | RD | Maximum value (float): voltage L3-N | V
Maximum values | 4 | 3006 | float | RD | Maximum value (float): voltage L1-L2 | V
Maximum values | 4 | 3008 | float | RD | Maximum value (float): voltage L2-L3 | V
Maximum values | 4 | 3010 | float | RD | Maximum value (float): voltage L3-L1 | V
Maximum values | 4 | 3012 | float | RD | Maximum value (float): current L1 | A
Maximum values | 4 | 3014 | float | RD | Maximum value (float): current L2 | A
Maximum values | 4 | 3016 | float | RD | Maximum value (float): current L3 | A
Maximum values | 4 | 3018 | float | RD | Maximum value (float): current sum | A
Maximum values | 4 | 3020 | float | RD | Maximum value (float): active power L1 | W
Maximum values | 4 | 3022 | float | RD | Maximum value (float): active power L2 | W
Maximum values | 4 | 3024 | float | RD | Maximum value (float): active power L3 | W
Maximum values | 4 | 3026 | float | RD | Maximum value (float): active power sum | W
Maximum values | 4 | 3028 | float | RD | Maximum value (float): reactive power L1 | var
Maximum values | 4 | 3030 | float | RD | Maximum value (float): reactive power L2 | var
Maximum values | 4 | 3032 | float | RD | Maximum value (float): reactive power L3 | var
Maximum values | 4 | 3034 | float | RD | Maximum value (float): reactive power sum | var
Maximum values | 4 | 3036 | float | RD | Maximum value (float): apparent power L1 | VA
Maximum values | 4 | 3038 | float | RD | Maximum value (float): apparent power L2 | VA
Maximum values | 4 | 3040 | float | RD | Maximum value (float): apparent power L3 | VA
Maximum values | 4 | 3042 | float | RD | Maximum value (float): apparent power sum | VA
Maximum values | 4 | 3044 | float | RD | Maximum value (float): cos(ϕ) L1
Maximum values | 4 | 3046 | float | RD | Maximum value (float): cos(ϕ) L2
Maximum values | 4 | 3048 | float | RD | Maximum value (float): cos(ϕ) L3
Maximum values | 4 | 3050 | float | RD | Maximum value (float): cos(ϕ) sum
Maximum values | 4 | 3052 | float | RD | Maximum value (float): active power, fundamental oscillation L1 | V
Maximum values | 4 | 3054 | float | RD | Maximum value (float): active power, fundamental oscillation L2 | V
Maximum values | 4 | 3056 | float | RD | Maximum value (float): active power, fundamental oscillation L3 | V
Maximum values | 4 | 3214 | float | RD | Maximum value (float): THD voltage L1 | %
Maximum values | 4 | 3216 | float | RD | Maximum value (float): THD voltage L2 | %
Maximum values | 4 | 3218 | float | RD | Maximum value (float): THD voltage L3 | %
Maximum values | 4 | 3220 | float | RD | Maximum value (float): THD current L1 | %
Maximum values | 4 | 3222 | float | RD | Maximum value (float): THD current L2 | %
Maximum values | 4 | 3224 | float | RD | Maximum value (float): THD current L3 | %
Maximum values | 4 | 3226 | float | RD | Maximum value (float): frequency | Hz
Maximum values | 4 | 3228 | float | RD | Maximum value (float): voltage zero sequence
Maximum values | 4 | 3230 | float | RD | Maximum value (float): voltage positive sequence
Maximum values | 4 | 3232 | float | RD | Maximum value (float): voltage negative sequence
Maximum values | 4 | 3234 | float | RD | Maximum value (float): current zero sequence
Maximum values | 4 | 3236 | float | RD | Maximum value (float): current positive sequence
Maximum values | 4 | 3238 | float | RD | Maximum value (float): current negative sequence
Maximum values | 4 | 3240 | float | RD | Maximum value (float): distortion power L1 | var
Maximum values | 4 | 3242 | float | RD | Maximum value (float): distortion power L2 | var
Maximum values | 4 | 3244 | float | RD | Maximum value (float): distortion power L3 | var
Maximum values | 4 | 3246 | float | RD | Maximum value (float): distortion power sum | var
Maximum values | 4 | 3264 | float | RD | Maximum value (float): TDD current L1 [%] | %
Maximum values | 4 | 3266 | float | RD | Maximum value (float): TDD current L2 [%] | %
Maximum values | 4 | 3268 | float | RD | Maximum value (float): TDD current L3 [%] | %
Maximum values | 4 | 3270 | float | RD | Maximum value (float): max. value power factor L1
Maximum values | 4 | 3272 | float | RD | Maximum value (float): max. value power factor L2
Maximum values | 4 | 3274 | float | RD | Maximum value (float): max. value power factor L3
Maximum values | 4 | 3276 | float | RD | Maximum value (float): max. value power factor sum3=Psum3/Ssum3
Maximum values | 4 | 3278 | float | RD | Maximum value (float): voltage asymmetry [%] (max) | %
Maximum values | 4 | 3280 | float | RD | Maximum value (float): current asymmetry [%] (max) | %
Maximum values | 4 | 13000 | short (x10) | RD | Maximum value (short): voltage L1-N | V
Maximum values | 4 | 13001 | short (x10) | RD | Maximum value (short): voltage L2-N | V
Maximum values | 4 | 13002 | short (x10) | RD | Maximum value (short): voltage L3-N | V
Maximum values | 4 | 13003 | short (x10) | RD | Maximum value (short): voltage L1-L2 | V
Maximum values | 4 | 13004 | short (x10) | RD | Maximum value (short): voltage L2-L3 | V
Maximum values | 4 | 13005 | short (x10) | RD | Maximum value (short): voltage L3-L1 | V
Maximum values | 4 | 13006 | short (x1000) | RD | Maximum value (short): current L1 | A
Maximum values | 4 | 13007 | short (x1000) | RD | Maximum value (short): current L2 | A
Maximum values | 4 | 13008 | short (x1000) | RD | Maximum value (short): current L3 | A
Maximum values | 4 | 13009 | short (x1000) | RD | Maximum value (short): current sum | A
Maximum values | 4 | 13010 | short (x10) | RD | Maximum value (short): active power L1 | W
Maximum values | 4 | 13011 | short (x10) | RD | Maximum value (short): active power L2 | W
Maximum values | 4 | 13012 | short (x10) | RD | Maximum value (short): active power L3 | W
Maximum values | 4 | 13013 | short | RD | Maximum value (short): active power sum | W
Maximum values | 4 | 13014 | short (x10) | RD | Maximum value (short): reactive power L1 | var
Maximum values | 4 | 13015 | short (x10) | RD | Maximum value (short): reactive power L2 | var
Maximum values | 4 | 13016 | short (x10) | RD | Maximum value (short): reactive power L3 | var
Maximum values | 4 | 13017 | short | RD | Maximum value (short): reactive power sum | var
Maximum values | 4 | 13018 | short (x10) | RD | Maximum value (short): apparent power L1 | VA
Maximum values | 4 | 13019 | short (x10) | RD | Maximum value (short): apparent power L2 | VA
Maximum values | 4 | 13020 | short (x10) | RD | Maximum value (short): apparent power L3 | VA
Maximum values | 4 | 13021 | short | RD | Maximum value (short): apparent power sum | VA
Maximum values | 4 | 13022 | short (x1000) | RD | Maximum value (short): cos(ϕ) L1
Maximum values | 4 | 13023 | short (x1000) | RD | Maximum value (short): cos(ϕ) L2
Maximum values | 4 | 13024 | short (x1000) | RD | Maximum value (short): cos(ϕ) L3
Maximum values | 4 | 13025 | short (x1000) | RD | Maximum value (short): cos(ϕ) sum
Maximum values | 4 | 13026 | short (x10) | RD | Maximum value (short): active power of fundamental oscillation L1 | W
Maximum values | 4 | 13027 | short (x10) | RD | Maximum value (short): active power of fundamental oscillation L2 | W
Maximum values | 4 | 13028 | short (x10) | RD | Maximum value (short): active power of fundamental oscillation L3 | W
Maximum values | 4 | 13107 | short (x100) | RD | Maximum value (short): THD voltage L1 | %
Maximum values | 4 | 13108 | short (x100) | RD | Maximum value (short): THD voltage L2 | %
Maximum values | 4 | 13109 | short (x100) | RD | Maximum value (short): THD voltage L3 | %
Maximum values | 4 | 13110 | short (x100) | RD | Maximum value (short): THD current L1 | %
Maximum values | 4 | 13111 | short (x100) | RD | Maximum value (short): THD current L2 | %
Maximum values | 4 | 13112 | short (x100) | RD | Maximum value (short): THD current L3 | %
Maximum values | 4 | 13113 | short (x100) | RD | Maximum value (short): frequency
Maximum values | 4 | 13114 | short (x10) | RD | Maximum value (short): voltage zero sequence
Maximum values | 4 | 13115 | short (x10) | RD | Maximum value (short): voltage positive sequence
Maximum values | 4 | 13116 | short (x10) | RD | Maximum value (short): voltage negative sequence
Maximum values | 4 | 13117 | short (x1000) | RD | Maximum value (short): current zero sequence
Maximum values | 4 | 13118 | short (x1000) | RD | Maximum value (short): current positive sequence
Maximum values | 4 | 13119 | short (x1000) | RD | Maximum value (short): current negative sequence
Maximum values | 4 | 13120 | short (x10) | RD | Maximum value (short): distortion power L1 | var
Maximum values | 4 | 13121 | short (x10) | RD | Maximum value (short): distortion power L2 | var
Maximum values | 4 | 13122 | short (x10) | RD | Maximum value (short): distortion power L3 | var
Maximum values | 4 | 13123 | short (x10) | RD | Maximum value (short): distortion power sum | var
Maximum values, timestamp | 6 | 3300 | uint | RD | UTC timestamp of max. value: voltage L1-N | s
Maximum values, timestamp | 6 | 3302 | uint | RD | UTC timestamp of max. value: voltage L2-N | s
Maximum values, timestamp | 6 | 3304 | uint | RD | UTC timestamp of max. value: voltage L3-N | s
Maximum values, timestamp | 6 | 3306 | uint | RD | UTC timestamp of max. value: voltage L1-L2 | s
Maximum values, timestamp | 6 | 3308 | uint | RD | UTC timestamp of max. value: voltage L2-L3 | s
Maximum values, timestamp | 6 | 3310 | uint | RD | UTC timestamp of max. value: voltage L3-L1 | s
Maximum values, timestamp | 6 | 3312 | uint | RD | UTC timestamp of max. value: current L1 | s
Maximum values, timestamp | 6 | 3314 | uint | RD | UTC timestamp of max. value: current L2 | s
Maximum values, timestamp | 6 | 3316 | uint | RD | UTC timestamp of max. value: current L3 | s
Maximum values, timestamp | 6 | 3318 | uint | RD | UTC timestamp of max. value: current sum | s
Maximum values, timestamp | 6 | 3320 | uint | RD | UTC timestamp of max. value: active power L1 | s
Maximum values, timestamp | 6 | 3322 | uint | RD | UTC timestamp of max. value: active power L2 | s
Maximum values, timestamp | 6 | 3324 | uint | RD | UTC timestamp of max. value: active power L3 | s
Maximum values, timestamp | 6 | 3326 | uint | RD | UTC timestamp of max. value: active power sum | s
Maximum values, timestamp | 6 | 3328 | uint | RD | UTC timestamp of max. value: reactive power L1 | s
Maximum values, timestamp | 6 | 3330 | uint | RD | UTC timestamp of max. value: reactive power L2 | s
Maximum values, timestamp | 6 | 3332 | uint | RD | UTC timestamp of max. value: reactive power L3 | s
Maximum values, timestamp | 6 | 3334 | uint | RD | UTC timestamp of max. value: reactive power sum | s
Maximum values, timestamp | 6 | 3336 | uint | RD | UTC timestamp of max. value: apparent power L1 | s
Maximum values, timestamp | 6 | 3338 | uint | RD | UTC timestamp of max. value: apparent power L2 | s
Maximum values, timestamp | 6 | 3340 | uint | RD | UTC timestamp of max. value: apparent power L3 | s
Maximum values, timestamp | 6 | 3342 | uint | RD | UTC timestamp of max. value: apparent power sum | s
Maximum values, timestamp | 6 | 3344 | uint | RD | UTC timestamp of max. value: cos(ϕ) L1 | s
Maximum values, timestamp | 6 | 3346 | uint | RD | UTC timestamp of max. value: cos(ϕ) L2 | s
Maximum values, timestamp | 6 | 3348 | uint | RD | UTC timestamp of max. value: cos(ϕ) L3 | s
Maximum values, timestamp | 6 | 3350 | uint | RD | UTC timestamp of max. value: cos(ϕ) sum | s
Maximum values, timestamp | 6 | 3352 | uint | RD | UTC timestamp of max. value: active power (fundamental oscillation) L1 | s
Maximum values, timestamp | 6 | 3354 | uint | RD | UTC timestamp of max. value: active power (fundamental oscillation) L2 | s
Maximum values, timestamp | 6 | 3356 | uint | RD | UTC timestamp of max. value: active power (fundamental oscillation) L3 | s
Maximum values, timestamp | 6 | 3514 | uint | RD | UTC timestamp of max. value: THD voltage L1 | s
Maximum values, timestamp | 6 | 3516 | uint | RD | UTC timestamp of max. value: THD voltage L2 | s
Maximum values, timestamp | 6 | 3518 | uint | RD | UTC timestamp of max. value: THD voltage L3 | s
Maximum values, timestamp | 6 | 3520 | uint | RD | UTC timestamp of max. value: THD current L1 | s
Maximum values, timestamp | 6 | 3522 | uint | RD | UTC timestamp of max. value: THD current L2 | s
Maximum values, timestamp | 6 | 3524 | uint | RD | UTC timestamp of max. value: THD current L3 | s
Maximum values, timestamp | 6 | 3526 | uint | RD | UTC timestamp of max. value: frequency | s
Maximum values, timestamp | 6 | 3528 | uint | RD | UTC timestamp of max. value: voltage zero sequence | s
Maximum values, timestamp | 6 | 3530 | uint | RD | UTC timestamp of max. value: voltage positive sequence | s
Maximum values, timestamp | 6 | 3532 | uint | RD | UTC timestamp of max. value: voltage negative sequence | s
Maximum values, timestamp | 6 | 3534 | uint | RD | UTC timestamp of max. value: current zero sequence | s
Maximum values, timestamp | 6 | 3536 | uint | RD | UTC timestamp of max. value: current positive sequence | s
Maximum values, timestamp | 6 | 3538 | uint | RD | UTC timestamp of max. value: current negative sequence | s
Maximum values, timestamp | 6 | 3540 | uint | RD | UTC timestamp of max. value: distortion power L1 | s
Maximum values, timestamp | 6 | 3542 | uint | RD | UTC timestamp of max. value: distortion power L2 | s
Maximum values, timestamp | 6 | 3544 | uint | RD | UTC timestamp of max. value: distortion power L3 | s
Maximum values, timestamp | 6 | 3546 | uint | RD | UTC timestamp of max. value: distortion power sum | s
Maximum values, timestamp | 6 | 3548 | uint | RD | UTC timestamp of max. value: mean value current L1 | s
Maximum values, timestamp | 6 | 3550 | uint | RD | UTC timestamp of max. value: mean value current L2 | s
Maximum values, timestamp | 6 | 3552 | uint | RD | UTC timestamp of max. value: mean value current L3 | s
Maximum values, timestamp | 6 | 3554 | uint | RD | UTC timestamp of max. value: mean value current sum | s
Maximum values, timestamp | 6 | 3556 | uint | RD | UTC timestamp of max. value: mean value active power L1 | s
Maximum values, timestamp | 6 | 3558 | uint | RD | UTC timestamp of max. value: mean value active power L2 | s
Maximum values, timestamp | 6 | 3560 | uint | RD | UTC timestamp of max. value: mean value active power L3 | s
Maximum values, timestamp | 6 | 3562 | uint | RD | UTC timestamp of max. value: mean value active power sum | s
Maximum values, timestamp | 6 | 3564 | uint | RD | UTC timestamp of max. value: TDD current L1 | s
Maximum values, timestamp | 6 | 3566 | uint | RD | UTC timestamp of max. value: TDD current L2 | s
Maximum values, timestamp | 6 | 3568 | uint | RD | UTC timestamp of max. value: TDD current L3 | s
Maximum values, timestamp | 6 | 3570 | uint | RD | UTC timestamp of max. value: power factor L1 | s
Maximum values, timestamp | 6 | 3572 | uint | RD | UTC timestamp of max. value: power factor L2 | s
Maximum values, timestamp | 6 | 3574 | uint | RD | UTC timestamp of max. value: power factor L3 | s
Maximum values, timestamp | 6 | 3576 | uint | RD | UTC timestamp of max. value: power factor sum3=Psum3/Ssum3 | s
Maximum values, timestamp | 6 | 3578 | uint | RD | UTC timestamp of max. value: Voltage asymmetry | s
Maximum values, timestamp | 6 | 3580 | uint | RD | UTC timestamp of max. value: Current asymmetry | s
Minimum values | 7 | 4000 | float | RD | Minimum value (float): voltage L1-N | V
Minimum values | 7 | 4002 | float | RD | Minimum value (float): voltage L2-N | V
Minimum values | 7 | 4004 | float | RD | Minimum value (float): voltage L3-N | V
Minimum values | 7 | 4006 | float | RD | Minimum value (float): voltage L1-L2 | V
Minimum values | 7 | 4008 | float | RD | Minimum value (float): voltage L1-L3 | V
Minimum values | 7 | 4010 | float | RD | Minimum value (float): voltage L3-L1 | V
Minimum values | 7 | 4012 | float | RD | Minimum value (float): cos(ϕ) L1
Minimum values | 7 | 4014 | float | RD | Minimum value (float): cos(ϕ) L2
Minimum values | 7 | 4016 | float | RD | Minimum value (float): cos(ϕ) L3
Minimum values | 7 | 4018 | float | RD | Minimum value (float): cos(ϕ) sum
Minimum values | 7 | 4098 | float | RD | Minimum value (float): THD voltage L1 [%] | %
Minimum values | 7 | 4100 | float | RD | Minimum value (float): THD voltage L2 [%] | %
Minimum values | 7 | 4102 | float | RD | Minimum value (float): THD voltage L3 [%] | %
Minimum values | 7 | 4104 | float | RD | Minimum value (float): frequency | Hz
Minimum values | 7 | 4106 | float | RD | Minimum value (float): voltage zero sequence
Minimum values | 7 | 4108 | float | RD | Minimum value (float): voltage positive sequence
Minimum values | 7 | 4110 | float | RD | Minimum value (float): voltage negative sequence
Minimum values | 7 | 4112 | float | RD | Minimum value (float): active power L1 | W
Minimum values | 7 | 4114 | float | RD | Minimum value (float): active power L2 | W
Minimum values | 7 | 4116 | float | RD | Minimum value (float): active power L3 | W
Minimum values | 7 | 4118 | float | RD | Minimum value (float): active power sum | W
Minimum values | 7 | 4120 | float | RD | Minimum value (float): power factor L1
Minimum values | 7 | 4122 | float | RD | Minimum value (float): power factor L2
Minimum values | 7 | 4124 | float | RD | Minimum value (float): power factor L3
Minimum values | 7 | 4126 | float | RD | Minimum value (float): power factor sum3=Psum3/Ssum3
Minimum values | 7 | 4128 | float | RD | Minimum value (float): THD current L1 [%] | %
Minimum values | 7 | 4130 | float | RD | Minimum value (float): THD current L2 [%] | %
Minimum values | 7 | 4132 | float | RD | Minimum value (float): THD current L3 [%] | %
Minimum values | 7 | 4134 | float | RD | Minimum value (float): current L1 | A
Minimum values | 7 | 4136 | float | RD | Minimum value (float): current L2 | A
Minimum values | 7 | 4138 | float | RD | Minimum value (float): current L3 | A
Minimum values | 7 | 4140 | float | RD | Minimum value (float): current sum | A
Minimum values | 7 | 4142 | float | RD | Minimum value (float): reactive power L1 | var
Minimum values | 7 | 4144 | float | RD | Minimum value (float): reactive power L2 | var
Minimum values | 7 | 4146 | float | RD | Minimum value (float): reactive power L3 | var
Minimum values | 7 | 4148 | float | RD | Minimum value (float): reactive power sum | var
Minimum values | 7 | 4150 | float | RD | Minimum value (float): apparent power L1 | VA
Minimum values | 7 | 4152 | float | RD | Minimum value (float): apparent power L2 | VA
Minimum values | 7 | 4154 | float | RD | Minimum value (float): apparent power L3 | VA
Minimum values | 7 | 4156 | float | RD | Minimum value (float): apparent power sum | VA
Minimum values | 7 | 4158 | float | RD | Minimum value (float): voltage asymmetry [%] (min) | %
Minimum values | 7 | 4160 | float | RD | Minimum value (float): current asymmetry [%] (min) | %
Minimum values | 7 | 14000 | short (x10) | RD | Minimum value (short): voltage L1-N | V
Minimum values | 7 | 14001 | short (x10) | RD | Minimum value (short): voltage L2-N | V
Minimum values | 7 | 14002 | short (x10) | RD | Minimum value (short): voltage L3-N | V
Minimum values | 7 | 14003 | short (x10) | RD | Minimum value (short): voltage L1-L2 | V
Minimum values | 7 | 14004 | short (x10) | RD | Minimum value (short): voltage L1-L3 | V
Minimum values | 7 | 14005 | short (x10) | RD | Minimum value (short): voltage L3-L1 | V
Minimum values | 7 | 14006 | short (x1000) | RD | Minimum value (short): cos(ϕ) L1
Minimum values | 7 | 14007 | short (x1000) | RD | Minimum value (short): cos(ϕ) L1
Minimum values | 7 | 14008 | short (x1000) | RD | Minimum value (short): cos(ϕ) L1
Minimum values | 7 | 14009 | short (x1000) | RD | Minimum value (short): cos(ϕ) L1
Minimum values | 7 | 14049 | short (x100) | RD | Minimum value (short): THD voltage L1 [%] | %
Minimum values | 7 | 14050 | short (x100) | RD | Minimum value (short): THD voltage L2 [%] | %
Minimum values | 7 | 14051 | short (x100) | RD | Minimum value (short): THD voltage L3 [%] | %
Minimum values | 7 | 14052 | short (x100) | RD | Minimum value (short): frequency | Hz
Minimum values | 7 | 14053 | short (x10) | RD | Minimum value (short): voltage zero sequence
Minimum values | 7 | 14054 | short (x10) | RD | Minimum value (short): voltage positive sequence
Minimum values | 7 | 14055 | short (x10) | RD | Minimum value (short): voltage negative sequence
Minimum values | 7 | 14056 | short (x10) | RD | Minimum value (short): active power L1 | W
Minimum values | 7 | 14057 | short (x10) | RD | Minimum value (short): active power L2 | W
Minimum values | 7 | 14058 | short (x10) | RD | Minimum value (short): active power L3 | W
Minimum values | 7 | 14059 | short (x10) | RD | Minimum value (short): active power sum | W
Minimum values, timestamp | 9 | 4200 | uint | RD | UTC timestamp of min. value: voltage L1-N | s
Minimum values, timestamp | 9 | 4202 | uint | RD | UTC timestamp of min. value: voltage L2-N | s
Minimum values, timestamp | 9 | 4204 | uint | RD | UTC timestamp of min. value: voltage L3-N | s
Minimum values, timestamp | 9 | 4206 | uint | RD | UTC timestamp of min. value: voltage L1-L2 | s
Minimum values, timestamp | 9 | 4208 | uint | RD | UTC timestamp of min. value: voltage L2-L3 | s
Minimum values, timestamp | 9 | 4210 | uint | RD | UTC timestamp of min. value: voltage L3-L1 | s
Minimum values, timestamp | 9 | 4212 | uint | RD | UTC timestamp of min. value: cos(ϕ) L1 | s
Minimum values, timestamp | 9 | 4214 | uint | RD | UTC timestamp of min. value: cos(ϕ) L2 | s
Minimum values, timestamp | 9 | 4216 | uint | RD | UTC timestamp of min. value: cos(ϕ) L3 | s
Minimum values, timestamp | 9 | 4218 | uint | RD | UTC timestamp of min. value: cos(ϕ) sum | s
Minimum values, timestamp | 9 | 4298 | uint | RD | UTC timestamp of min. value: THD voltage L1 | s
Minimum values, timestamp | 9 | 4300 | uint | RD | UTC timestamp of min. value: THD voltage L2 | s
Minimum values, timestamp | 9 | 4302 | uint | RD | UTC timestamp of min. value: THD voltage L3 | s
Minimum values, timestamp | 9 | 4304 | uint | RD | UTC timestamp of min. value: frequency | s
Minimum values, timestamp | 9 | 4306 | uint | RD | UTC timestamp of min. value: voltage zero sequence | s
Minimum values, timestamp | 9 | 4308 | uint | RD | UTC timestamp of min. value: voltage positive sequence | s
Minimum values, timestamp | 9 | 4310 | uint | RD | UTC timestamp of min. value: voltage negative sequence | s
Minimum values, timestamp | 9 | 4312 | uint | RD | UTC timestamp of min. value: active power L1 | s
Minimum values, timestamp | 9 | 4314 | uint | RD | UTC timestamp of min. value: active power L2 | s
Minimum values, timestamp | 9 | 4316 | uint | RD | UTC timestamp of min. value: active power L3 | s
Minimum values, timestamp | 9 | 4318 | uint | RD | UTC timestamp of min. value: active power sum | s
Minimum values, timestamp | 9 | 4320 | uint | RD | UTC timestamp of min. value: power factor L1 | s
Minimum values, timestamp | 9 | 4322 | uint | RD | UTC timestamp of min. value: power factor L2 | s
Minimum values, timestamp | 9 | 4324 | uint | RD | UTC timestamp of min. value: power factor L3 | s
Minimum values, timestamp | 9 | 4326 | uint | RD | UTC timestamp of min. value: power factor sum | s
Minimum values, timestamp | 9 | 4328 | uint | RD | UTC timestamp of min. value: THD current L1 | s
Minimum values, timestamp | 9 | 4330 | uint | RD | UTC timestamp of min. value: THD current L2 | s
Minimum values, timestamp | 9 | 4332 | uint | RD | UTC timestamp of min. value: THD current L3 | s
Minimum values, timestamp | 9 | 4334 | uint | RD | UTC timestamp of min. value: current L1 | s
Minimum values, timestamp | 9 | 4336 | uint | RD | UTC timestamp of min. value: current L2 | s
Minimum values, timestamp | 9 | 4338 | uint | RD | UTC timestamp of min. value: current L3 | s
Minimum values, timestamp | 9 | 4340 | uint | RD | UTC timestamp of min. value: current sum | s
Minimum values, timestamp | 9 | 4342 | uint | RD | UTC timestamp of min. value: reactive power L1 | s
Minimum values, timestamp | 9 | 4344 | uint | RD | UTC timestamp of min. value: reactive power L2 | s
Minimum values, timestamp | 9 | 4346 | uint | RD | UTC timestamp of min. value: reactive power L3 | s
Minimum values, timestamp | 9 | 4348 | uint | RD | UTC timestamp of min. value: reactive power sum | s
Minimum values, timestamp | 9 | 4350 | uint | RD | UTC timestamp of min. value: apparent power L1 | s
Minimum values, timestamp | 9 | 4352 | uint | RD | UTC timestamp of min. value: apparent power L2 | s
Minimum values, timestamp | 9 | 4354 | uint | RD | UTC timestamp of min. value: apparent power L3 | s
Minimum values, timestamp | 9 | 4356 | uint | RD | UTC timestamp of min. value: apparent power sum | s
Minimum values, timestamp | 9 | 4358 | uint | RD | UTC timestamp of min. value: voltage asymmetry | s
Minimum values, timestamp | 9 | 4360 | uint | RD | UTC timestamp of min. value: current asymmetry | s
Moving mean values | 12 | 57 | char | RD/WR | Time base moving mean values - Current 0=5s, 1=10s, 2=30s, 3=60s, 4=5min, 5=8min, 6=15min |  | 0 | 6
Moving mean values | 12 | 58 | char | RD/WR | Time base moving mean values - Power 0=5s, 1=10s, 2=30s, 3=60s, 4=5min, 5=8min, 6=15min |  | 0 | 6
Moving mean values | 12 | 2000 | float | RD | Mean value (float): voltage L1 | V
Moving mean values | 12 | 2002 | float | RD | Mean value (float): voltage L2 | V
Moving mean values | 12 | 2004 | float | RD | Mean value (float): voltage L3 | V
Moving mean values | 12 | 2006 | float | RD | Mean value (float): mean value voltage L1-L2 | V
Moving mean values | 12 | 2008 | float | RD | Mean value (float): mean value voltage L2-L3 | V
Moving mean values | 12 | 2010 | float | RD | Mean value (float): mean value voltage L3-L1 | V
Moving mean values | 12 | 2012 | float | RD | Mean value (float): mean value current L1 | A
Moving mean values | 12 | 2014 | float | RD | Mean value (float): mean value current L2 | A
Moving mean values | 12 | 2016 | float | RD | Mean value (float): mean value current L3 | A
Moving mean values | 12 | 2018 | float | RD | Mean value (float): mean value current sum | A
Moving mean values | 12 | 2020 | float | RD | Mean value (float): mean value active power L1 | W
Moving mean values | 12 | 2022 | float | RD | Mean value (float): mean value active power L2 | W
Moving mean values | 12 | 2024 | float | RD | Mean value (float): mean value active power L3 | W
Moving mean values | 12 | 2026 | float | RD | Mean value (float): mean value active power sum | W
Moving mean values | 12 | 2028 | float | RD | Mean value (float): mean value reactive power L1 | var
Moving mean values | 12 | 2030 | float | RD | Mean value (float): reactive power L2 | var
Moving mean values | 12 | 2032 | float | RD | Mean value (float): reactive power L3 | var
Moving mean values | 12 | 2034 | float | RD | Mean value (float): mean value reactive power sum | var
Moving mean values | 12 | 2036 | float | RD | Mean value (float): apparent power L1 | VA
Moving mean values | 12 | 2038 | float | RD | Mean value (float): mean value apparent power L2 | VA
Moving mean values | 12 | 2040 | float | RD | Mean value (float): mean value apparent power L3 | VA
Moving mean values | 12 | 2042 | float | RD | Mean value (float): mean value apparent power sum | VA
Moving mean values | 12 | 2044 | float | RD | Mean value (float): mean value cos(ϕ) L1
Moving mean values | 12 | 2046 | float | RD | Mean value (float): mean value cos(ϕ) L2
Moving mean values | 12 | 2048 | float | RD | Mean value (float): mean value cos(ϕ) L3
Moving mean values | 12 | 2050 | float | RD | Mean value (float): cos(ϕ) sum
Moving mean values | 12 | 2052 | float | RD | Mean value (float): active power, fundamental oscillation L1 | W
Moving mean values | 12 | 2054 | float | RD | Mean value (float): active power, fundamental oscillation L2 | W
Moving mean values | 12 | 2056 | float | RD | Mean value (float): active power, fundamental oscillation L3 | W
Moving mean values | 12 | 2214 | float | RD | Mean value (float): THD voltage L1 [%] | %
Moving mean values | 12 | 2216 | float | RD | Mean value (float): THD voltage L2 [%] | %
Moving mean values | 12 | 2218 | float | RD | Mean value (float): THD voltage L3 [%] | %
Moving mean values | 12 | 2220 | float | RD | Mean value (float): THD current L1 [%] | %
Moving mean values | 12 | 2222 | float | RD | Mean value (float): THD current L2 [%] | %
Moving mean values | 12 | 2224 | float | RD | Mean value (float): THD current L3 [%] | %
Moving mean values | 12 | 2226 | float | RD | Mean value (float): frequency | Hz
Moving mean values | 12 | 2228 | float | RD | Mean value (float): zero sequence voltage
Moving mean values | 12 | 2230 | float | RD | Mean value (float): positive sequence voltage
Moving mean values | 12 | 2232 | float | RD | Mean value (float): negative sequence voltage
Moving mean values | 12 | 2234 | float | RD | Mean value (float): zero sequence current
Moving mean values | 12 | 2236 | float | RD | Mean value (float): mean value positive sequence current
Moving mean values | 12 | 2238 | float | RD | Mean value (float): mean value negative sequence current
Moving mean values | 12 | 2240 | float | RD | Mean value (float): mean value distortion power L1 | var
Moving mean values | 12 | 2242 | float | RD | Mean value (float): mean value distortion power L2 | var
Moving mean values | 12 | 2244 | float | RD | Mean value (float): distortion power L3 | var
Moving mean values | 12 | 2246 | float | RD | Mean value (float): distortion power sum | var
Moving mean values | 12 | 2248 | float | RD | Mean value (float): TDD (total demand distortion) current L1 [%] | %
Moving mean values | 12 | 2250 | float | RD | Mean value (float): TDD (total demand distortion) current L2 [%] | %
Moving mean values | 12 | 2252 | float | RD | Mean value (float): TDD (total demand distortion) current L3 [%] | %
Moving mean values | 12 | 2254 | float | RD | Mean value (float): power factor L1
Moving mean values | 12 | 2256 | float | RD | Mean value (float): power factor L2
Moving mean values | 12 | 2258 | float | RD | Mean value (float): power factor L3
Moving mean values | 12 | 2260 | float | RD | Mean value (float): power factor sum3=Psum3/Ssum3
Moving mean values | 12 | 2294 | float | RD | Mean value (float): voltage asymmetry [%] (avg) | %
Moving mean values | 12 | 2296 | float | RD | Mean value (float): current asymmetry [%] (avg) | %
Moving mean values | 12 | 12000 | short (x10) | RD | Mean value (short): voltage L1-N | V
Moving mean values | 12 | 12001 | short (x10) | RD | Mean value (short): voltage L2-N | V
Moving mean values | 12 | 12002 | short (x10) | RD | Mean value (short): voltage L3-N | V
Moving mean values | 12 | 12003 | short (x10) | RD | Mean value (short): voltage L1-L2 | V
Moving mean values | 12 | 12004 | short (x10) | RD | Mean value (short): voltage L2-L3 | V
Moving mean values | 12 | 12005 | short (x10) | RD | Mean value (short): voltage L3-L1 | V
Moving mean values | 12 | 12006 | short (x1000) | RD | Mean value (short): current L1 | A
Moving mean values | 12 | 12007 | short (x1000) | RD | Mean value (short): current L2 | A
Moving mean values | 12 | 12008 | short (x1000) | RD | Mean value (short): current L3 | A
Moving mean values | 12 | 12009 | short (x1000) | RD | Mean value (short): current sum | A
Moving mean values | 12 | 12010 | short (x10) | RD | Mean value (short): active power L1 | W
Moving mean values | 12 | 12011 | short (x10) | RD | Mean value (short): active power L2 | W
Moving mean values | 12 | 12012 | short (x10) | RD | Mean value (short): active power L3 | W
Moving mean values | 12 | 12013 | short | RD | Mean value (short): active power sum | W
Moving mean values | 12 | 12014 | short (x10) | RD | Mean value (short): reactive power L1 | var
Moving mean values | 12 | 12015 | short (x10) | RD | Mean value (short): reactive power L2 | var
Moving mean values | 12 | 12016 | short (x10) | RD | Mean value (short): reactive power L3 | var
Moving mean values | 12 | 12017 | short | RD | Mean value (short): reactive power sum | var
Moving mean values | 12 | 12018 | short (x10) | RD | Mean value (short): apparent power L1 | VA
Moving mean values | 12 | 12019 | short (x10) | RD | Mean value (short): apparent power L2 | VA
Moving mean values | 12 | 12020 | short (x10) | RD | Mean value (short): apparent power L3 | VA
Moving mean values | 12 | 12021 | short | RD | Mean value (short): apparent power sum | VA
Moving mean values | 12 | 12022 | short (x1000) | RD | Mean value (short): cos(ϕ) L1
Moving mean values | 12 | 12023 | short (x1000) | RD | Mean value (short): cos(ϕ) L2
Moving mean values | 12 | 12024 | short (x1000) | RD | Mean value (short): cos(ϕ) L3
Moving mean values | 12 | 12025 | short (x1000) | RD | Mean value (short): cos(ϕ) sum
Moving mean values | 12 | 12026 | short (x10) | RD | Mean value (short): active power of fundamental oscillation L1 | W
Moving mean values | 12 | 12027 | short (x10) | RD | Mean value (short): active power of fundamental oscillation L2 | W
Moving mean values | 12 | 12028 | short (x10) | RD | Mean value (short): active power of fundamental oscillation L3 | W
Moving mean values | 12 | 12107 | short (x100) | RD | Mean value (short): THD voltage L1 | %
Moving mean values | 12 | 12108 | short (x100) | RD | Mean value (short): THD voltage L2 | %
Moving mean values | 12 | 12109 | short (x100) | RD | Mean value (short): THD voltage L3 | %
Moving mean values | 12 | 12110 | short (x100) | RD | Mean value (short): THD current L1 | %
Moving mean values | 12 | 12111 | short (x100) | RD | Mean value (short): THD current L2 | %
Moving mean values | 12 | 12112 | short (x100) | RD | Mean value (short): THD current L3 | %
Moving mean values | 12 | 12113 | short (x100) | RD | Mean value (short): frequency | Hz
Moving mean values | 12 | 12114 | short (x10) | RD | Mean value (short): zero sequence voltage
Moving mean values | 12 | 12115 | short (x10) | RD | Mean value (short): positive sequence voltage
Moving mean values | 12 | 12116 | short (x10) | RD | Mean value (short): negative sequence voltage
Moving mean values | 12 | 12117 | short (x1000) | RD | Mean value (short): zero sequence current
Moving mean values | 12 | 12118 | short (x1000) | RD | Mean value (short): positive sequence current
Moving mean values | 12 | 12119 | short (x1000) | RD | Mean value (short): negative sequence current
Moving mean values | 12 | 12120 | short (x10) | RD | Mean value (short): distortion power L1 | var
Moving mean values | 12 | 12121 | short (x10) | RD | Mean value (short): distortion power L2 | var
Moving mean values | 12 | 12122 | short (x10) | RD | Mean value (short): distortion power L3 | var
Moving mean values | 12 | 12123 | short | RD | Mean value (short): distortion power sum | var
Maximum values of moving mean values | 14 | 3248 | float | RD | Maximum values of mean values (float): current L1 | A
Maximum values of moving mean values | 14 | 3250 | float | RD | Maximum values of mean values (float): current L2 | A
Maximum values of moving mean values | 14 | 3252 | float | RD | Maximum values of mean values (float): current L3 | A
Maximum values of moving mean values | 14 | 3254 | float | RD | Maximum values of mean values (float): current sum | A
Maximum values of moving mean values | 14 | 3256 | float | RD | Maximum values of mean values (float): active power L1 | W
Maximum values of moving mean values | 14 | 3258 | float | RD | Maximum values of mean values (float): active power L2 | W
Maximum values of moving mean values | 14 | 3260 | float | RD | Maximum values of mean values (float): active power L3 | W
Maximum values of moving mean values | 14 | 3262 | float | RD | Maximum values of mean values (float): active power sum | W
Maximum values of moving mean values | 14 | 13124 | short (x1000) | RD | Maximum values of mean values (short): current L1 | A
Maximum values of moving mean values | 14 | 13125 | short (x1000) | RD | Maximum values of mean values (short): current L2 | A
Maximum values of moving mean values | 14 | 13126 | short (x1000) | RD | Maximum values of mean values (short): current L3 | A
Maximum values of moving mean values | 14 | 13128 | short (x10) | RD | Maximum values of mean values (short): active power L1 | A
Maximum values of moving mean values | 14 | 13129 | short (x10) | RD | Maximum values of mean values (short): active power L2 | A
Maximum values of moving mean values | 14 | 13130 | short (x10) | RD | Maximum values of mean values (short): active power L3 | A
Gridded mean values | 16 | 31504 | ushort | RD/WR | averaging interval for Gridded Mean Values in Seconds | s | 60 | 3600
Gridded mean values | 16 | 32000 | float | RD | Gridded mean values (float): maximum voltage L1 | V
Gridded mean values | 16 | 32002 | float | RD | Gridded mean values (float): maximum voltage L2 | V
Gridded mean values | 16 | 32004 | float | RD | Gridded mean values (float): maximum voltage L3 | V
Gridded mean values | 16 | 32008 | float | RD | Gridded mean values (float): maximum voltage L1-L2 | V
Gridded mean values | 16 | 32010 | float | RD | Gridded mean values (float): maximum voltage L2-L3 | V
Gridded mean values | 16 | 32012 | float | RD | Gridded mean values (float): maximum voltage L3-L1 | V
Gridded mean values | 16 | 32016 | float | RD | Gridded mean values (float): maximum current L1 | A
Gridded mean values | 16 | 32018 | float | RD | Gridded mean values (float): maximum current L2 | A
Gridded mean values | 16 | 32020 | float | RD | Gridded mean values (float): maximum current L3 | A
Gridded mean values | 16 | 32022 | float | RD | Gridded mean values (float): maximum current L4 | A
Gridded mean values | 16 | 32024 | float | RD | Gridded mean values (float): sum maximum current L1-L3 | A
Gridded mean values | 16 | 32026 | float | RD | Gridded mean values (float): sum maximum current L1-L4 | A
Gridded mean values | 16 | 32028 | float | RD | Gridded mean values (float): maximum active power L1 | W
Gridded mean values | 16 | 32030 | float | RD | Gridded mean values (float): maximum active power L2 | W
Gridded mean values | 16 | 32032 | float | RD | Gridded mean values (float): maximum active power L3 | W
Gridded mean values | 16 | 32036 | float | RD | Gridded mean values (float): maximum total active power | W
Gridded mean values | 16 | 32040 | float | RD | Gridded mean values (float): maximum reactive power L1 | VA
Gridded mean values | 16 | 32042 | float | RD | Gridded mean values (float): maximum reactive power L2 | VA
Gridded mean values | 16 | 32044 | float | RD | Gridded mean values (float): maximum reactive power L3 | VA
Gridded mean values | 16 | 32048 | float | RD | Gridded mean values (float): maximum total reactive power | VA
Gridded mean values | 16 | 32052 | float | RD | Gridded mean values (float): maximum apparent power L1 | var
Gridded mean values | 16 | 32054 | float | RD | Gridded mean values (float): maximum apparent power L2 | var
Gridded mean values | 16 | 32056 | float | RD | Gridded mean values (float): maximum apparent power L3 | var
Gridded mean values | 16 | 32060 | float | RD | Gridded mean values (float): maximum total apparent power | var
Gridded mean values | 16 | 32064 | float | RD | Gridded mean values (float): maximum cos(phi) L1
Gridded mean values | 16 | 32066 | float | RD | Gridded mean values (float): maximum cos(phi) L2
Gridded mean values | 16 | 32068 | float | RD | Gridded mean values (float): maximum cos(phi) L3
Gridded mean values | 16 | 32072 | float | RD | Gridded mean values (float): maximum cos(phi)
Gridded mean values | 16 | 32076 | float | RD | Gridded mean values (float): minimum voltage L1 | V
Gridded mean values | 16 | 32078 | float | RD | Gridded mean values (float): minimum voltage L2 | V
Gridded mean values | 16 | 32080 | float | RD | Gridded mean values (float): minimum voltage L3 | V
Gridded mean values | 16 | 32084 | float | RD | Gridded mean values (float): minimum voltage L1-L2 | V
Gridded mean values | 16 | 32086 | float | RD | Gridded mean values (float): minimum voltage L2-L3 | V
Gridded mean values | 16 | 32088 | float | RD | Gridded mean values (float): minimum voltage L3-L1 | V
Gridded mean values | 16 | 32092 | float | RD | Gridded mean values (float): minimum current L1 | A
Gridded mean values | 16 | 32094 | float | RD | Gridded mean values (float): minimum current L2 | A
Gridded mean values | 16 | 32096 | float | RD | Gridded mean values (float): minimum current L3 | A
Gridded mean values | 16 | 32098 | float | RD | Gridded mean values (float): minimum current L4 | A
Gridded mean values | 16 | 32100 | float | RD | Gridded mean values (float): sum minimum current L1-L3 | A
Gridded mean values | 16 | 32102 | float | RD | Gridded mean values (float): sum minimum current L1-L4 | A
Gridded mean values | 16 | 32104 | float | RD | Gridded mean values (float): minimum active power L1 | W
Gridded mean values | 16 | 32106 | float | RD | Gridded mean values (float): minimum active power L2 | W
Gridded mean values | 16 | 32108 | float | RD | Gridded mean values (float): minimum active power L3 | W
Gridded mean values | 16 | 32112 | float | RD | Gridded mean values (float): minimum total active power | W
Gridded mean values | 16 | 32116 | float | RD | Gridded mean values (float): minimum reactive power L1 | VA
Gridded mean values | 16 | 32118 | float | RD | Gridded mean values (float): minimum reactive power L2 | VA
Gridded mean values | 16 | 32120 | float | RD | Gridded mean values (float): minimum reactive power L3 | VA
Gridded mean values | 16 | 32124 | float | RD | Gridded mean values (float): minimum total reactive power | VA
Gridded mean values | 16 | 32128 | float | RD | Gridded mean values (float): minimum apparent power L1 | var
Gridded mean values | 16 | 32130 | float | RD | Gridded mean values (float): minimum apparent power L2 | var
Gridded mean values | 16 | 32132 | float | RD | Gridded mean values (float): minimum apparent power L3 | var
Gridded mean values | 16 | 32136 | float | RD | Gridded mean values (float): minimum total apparent power | var
Gridded mean values | 16 | 32140 | float | RD | Gridded mean values (float): minimum cos(phi) L1
Gridded mean values | 16 | 32142 | float | RD | Gridded mean values (float): minimum cos(phi) L2
Gridded mean values | 16 | 32144 | float | RD | Gridded mean values (float): minimum cos(phi) L3
Gridded mean values | 16 | 32148 | float | RD | Gridded mean values (float): minimum cos(phi)
Gridded mean values | 16 | 32152 | float | RD | Gridded mean values (float): average voltage L1 | V
Gridded mean values | 16 | 32154 | float | RD | Gridded mean values (float): average voltage L2 | V
Gridded mean values | 16 | 32156 | float | RD | Gridded mean values (float): average voltage L3 | V
Gridded mean values | 16 | 32160 | float | RD | Gridded mean values (float): average voltage L1-L2 | V
Gridded mean values | 16 | 32162 | float | RD | Gridded mean values (float): average voltage L2-L3 | V
Gridded mean values | 16 | 32164 | float | RD | Gridded mean values (float): average voltage L3-L1 | V
Gridded mean values | 16 | 32168 | float | RD | Gridded mean values (float): average current L1 | A
Gridded mean values | 16 | 32170 | float | RD | Gridded mean values (float): average current L2 | A
Gridded mean values | 16 | 32172 | float | RD | Gridded mean values (float): average current L3 | A
Gridded mean values | 16 | 32174 | float | RD | Gridded mean values (float): average current L4 | A
Gridded mean values | 16 | 32176 | float | RD | Gridded mean values (float): sum average current L1-L3 | A
Gridded mean values | 16 | 32178 | float | RD | Gridded mean values (float): sum average current L1-L4 | A
Gridded mean values | 16 | 32180 | float | RD | Gridded mean values (float): average active power L1 | W
Gridded mean values | 16 | 32182 | float | RD | Gridded mean values (float): average active power L2 | W
Gridded mean values | 16 | 32184 | float | RD | Gridded mean values (float): average active power L3 | W
Gridded mean values | 16 | 32188 | float | RD | Gridded mean values (float): average total active power | W
Gridded mean values | 16 | 32192 | float | RD | Gridded mean values (float): average apparent power L1 | VA
Gridded mean values | 16 | 32194 | float | RD | Gridded mean values (float): average apparent power L2 | VA
Gridded mean values | 16 | 32196 | float | RD | Gridded mean values (float): average apparent power L3 | VA
Gridded mean values | 16 | 32200 | float | RD | Gridded mean values (float): average total apparent power | VA
Gridded mean values | 16 | 32204 | float | RD | Gridded mean values (float): average reactive power L1 | var
Gridded mean values | 16 | 32206 | float | RD | Gridded mean values (float): average reactive power L2 | var
Gridded mean values | 16 | 32208 | float | RD | Gridded mean values (float): average reactive power L3 | var
Gridded mean values | 16 | 32212 | float | RD | Gridded mean values (float): average total reactive power | var
Gridded mean values | 16 | 32216 | float | RD | Gridded mean values (float): average cos(phi) L1
Gridded mean values | 16 | 32218 | float | RD | Gridded mean values (float): average cos(phi) L2
Gridded mean values | 16 | 32220 | float | RD | Gridded mean values (float): average cos(phi) L3
Gridded mean values | 16 | 32224 | float | RD | Gridded mean values (float): average cos(phi)
Gridded mean values | 16 | 32609 | uint | RD | Gridded mean values (float): UTC timestamp
Drag indicator (peak indicator) | 17 | 7000 | float | RD | Drag indicator: highest value current L1 | A
Drag indicator (peak indicator) | 17 | 7002 | float | RD | Drag indicator: highest value current L2 | A
Drag indicator (peak indicator) | 17 | 7004 | float | RD | Drag indicator: highest value current L3 | A
Drag indicator (peak indicator) | 17 | 7006 | uint | RD | Drag indicator: point in time [UTC], highest value current L1 | s
Drag indicator (peak indicator) | 17 | 7008 | uint | RD | Drag indicator: point in time [UTC], highest value current L2 | s
Drag indicator (peak indicator) | 17 | 7010 | uint | RD | Drag indicator: point in time [UTC], highest value current L3 | s
Drag indicator (peak indicator) | 17 | 7012 | float | RD | Drag indicator: highest value apparent power L1 | VA
Drag indicator (peak indicator) | 17 | 7014 | float | RD | Drag indicator: highest value apparent power L2 | VA
Drag indicator (peak indicator) | 17 | 7016 | float | RD | Drag indicator: highest value apparent power L3 | VA
Drag indicator (peak indicator) | 17 | 7018 | float | RD | Drag indicator: highest value apparent power sum | VA
Drag indicator (peak indicator) | 17 | 7020 | uint | RD | Drag indicator: point in time [UTC], highest value apparent power L1 | s
Drag indicator (peak indicator) | 17 | 7022 | uint | RD | Drag indicator: point in time [UTC], highest value apparent power L2 | s
Drag indicator (peak indicator) | 17 | 7024 | uint | RD | Drag indicator: point in time [UTC], highest value apparent power L3 | s
Drag indicator (peak indicator) | 17 | 7026 | uint | RD | Drag indicator: point in time [UTC], highest value apparent power sum | s
Drag indicator (peak indicator) | 17 | 7028 | float | RD | Drag indicator: highest value active power L1, consumed | W
Drag indicator (peak indicator) | 17 | 7030 | float | RD | Drag indicator: highest value active power L2, consumed | W
Drag indicator (peak indicator) | 17 | 7032 | float | RD | Drag indicator: highest value active power L3, consumed | W
Drag indicator (peak indicator) | 17 | 7034 | float | RD | Drag indicator: highest value active power sum, consumed | W
Drag indicator (peak indicator) | 17 | 7036 | uint | RD | Drag indicator: point in time [UTC], highest value active power L1, consumed | s
Drag indicator (peak indicator) | 17 | 7038 | uint | RD | Drag indicator: point in time [UTC], highest value active power L2, consumed | s
Drag indicator (peak indicator) | 17 | 7040 | uint | RD | Drag indicator: point in time [UTC], highest value active power L3, consumed | s
Drag indicator (peak indicator) | 17 | 7042 | uint | RD | Drag indicator: point in time [UTC], highest value active power sum, consumed | s
Drag indicator (peak indicator) | 17 | 7044 | float | RD | Drag indicator: highest value active power L1, delivered | W
Drag indicator (peak indicator) | 17 | 7046 | float | RD | Drag indicator: highest value active power L2, delivered | W
Drag indicator (peak indicator) | 17 | 7048 | float | RD | Drag indicator: highest value active power L3, delivered | W
Drag indicator (peak indicator) | 17 | 7050 | float | RD | Drag indicator: highest value active power sum, delivered | W
Drag indicator (peak indicator) | 17 | 7052 | uint | RD | Drag indicator: point in time [UTC], highest value active power L1, delivered | s
Drag indicator (peak indicator) | 17 | 7054 | uint | RD | Drag indicator: point in time [UTC], highest value active power L2, delivered | s
Drag indicator (peak indicator) | 17 | 7056 | uint | RD | Drag indicator: point in time [UTC], highest value active power L3, delivered | s
Drag indicator (peak indicator) | 17 | 7058 | uint | RD | Drag indicator: point in time [UTC], highest value active power sum, delivered | s
Drag indicator (peak indicator) | 17 | 7060 | float | RD | Drag indicator: 2. highest value current L1 | A
Drag indicator (peak indicator) | 17 | 7062 | float | RD | Drag indicator: 2. highest value current L2 | A
Drag indicator (peak indicator) | 17 | 7064 | float | RD | Drag indicator: 2. highest value current L3 | A
Drag indicator (peak indicator) | 17 | 7066 | uint | RD | Drag indicator: point in time [UTC], 2. highest value current L1 | s
Drag indicator (peak indicator) | 17 | 7068 | uint | RD | Drag indicator: point in time [UTC], 2. highest value current L2 | s
Drag indicator (peak indicator) | 17 | 7070 | uint | RD | Drag indicator: point in time [UTC], 2. highest value current L3 | s
Drag indicator (peak indicator) | 17 | 7072 | float | RD | Drag indicator: 2. highest value apparent power L1 | VA
Drag indicator (peak indicator) | 17 | 7074 | float | RD | Drag indicator: 2. highest value apparent power L2 | VA
Drag indicator (peak indicator) | 17 | 7076 | float | RD | Drag indicator: 2. highest value apparent power L3 | VA
Drag indicator (peak indicator) | 17 | 7078 | float | RD | Drag indicator: 2. highest value apparent power sum | VA
Drag indicator (peak indicator) | 17 | 7080 | uint | RD | Drag indicator: point in time [UTC], 2. highest value apparent power L1 | s
Drag indicator (peak indicator) | 17 | 7082 | uint | RD | Drag indicator: point in time [UTC], 2. highest value apparent power L2 | s
Drag indicator (peak indicator) | 17 | 7084 | uint | RD | Drag indicator: point in time [UTC], 2. highest value apparent power L3 | s
Drag indicator (peak indicator) | 17 | 7086 | uint | RD | Drag indicator: point in time [UTC], 2. highest value apparent power sum | s
Drag indicator (peak indicator) | 17 | 7088 | float | RD | Drag indicator: 2. highest value active power L1, consumed | W
Drag indicator (peak indicator) | 17 | 7090 | float | RD | Drag indicator: 2. highest value active power L2, consumed | W
Drag indicator (peak indicator) | 17 | 7092 | float | RD | Drag indicator: 2. highest value active power L3, consumed | W
Drag indicator (peak indicator) | 17 | 7094 | float | RD | Drag indicator: 2. highest value active power sum, consumed | W
Drag indicator (peak indicator) | 17 | 7096 | uint | RD | Drag indicator: point in time [UTC], 2. highest value active power L1, consumed | s
Drag indicator (peak indicator) | 17 | 7098 | uint | RD | Drag indicator: point in time [UTC], 2. highest value active power L2, consumed | s
Drag indicator (peak indicator) | 17 | 7100 | uint | RD | Drag indicator: point in time [UTC], 2. highest value active power L3, consumed | s
Drag indicator (peak indicator) | 17 | 7102 | uint | RD | Drag indicator: point in time [UTC], 2. highest value active power sum, consumed | s
Drag indicator (peak indicator) | 17 | 7104 | float | RD | Drag indicator: 2. highest value active power L1, delivered | W
Drag indicator (peak indicator) | 17 | 7106 | float | RD | Drag indicator: 2. highest value active power L2, delivered | W
Drag indicator (peak indicator) | 17 | 7108 | float | RD | Drag indicator: 2. highest value active power L3, delivered | W
Drag indicator (peak indicator) | 17 | 7110 | float | RD | Drag indicator: 2. highest value active power sum, delivered | W
Drag indicator (peak indicator) | 17 | 7112 | uint | RD | Drag indicator: point in time [UTC], 2. highest value active power L1, delivered | s
Drag indicator (peak indicator) | 17 | 7114 | uint | RD | Drag indicator: point in time [UTC], 2. highest value active power L2, delivered | s
Drag indicator (peak indicator) | 17 | 7116 | uint | RD | Drag indicator: point in time [UTC], 2. highest value active power L3, delivered | s
Drag indicator (peak indicator) | 17 | 7118 | uint | RD | Drag indicator: point in time [UTC], 2. highest value active power sum, delivered | s
Drag indicator (peak indicator) | 17 | 7120 | float | RD | Drag indicator: 3. highest value current L1 | A
Drag indicator (peak indicator) | 17 | 7122 | float | RD | Drag indicator: 3. highest value current L2 | A
Drag indicator (peak indicator) | 17 | 7124 | float | RD | Drag indicator: 3. highest value current L3 | A
Drag indicator (peak indicator) | 17 | 7126 | uint | RD | Drag indicator: point in time [UTC], 3. highest value current L1 | s
Drag indicator (peak indicator) | 17 | 7128 | uint | RD | Drag indicator: point in time [UTC], 3. highest value current L2 | s
Drag indicator (peak indicator) | 17 | 7130 | uint | RD | Drag indicator: point in time [UTC], 3. highest value current L3 | s
Drag indicator (peak indicator) | 17 | 7132 | float | RD | Drag indicator: 3. highest value apparent power L1 | VA
Drag indicator (peak indicator) | 17 | 7134 | float | RD | Drag indicator: 3. highest value apparent power L2 | VA
Drag indicator (peak indicator) | 17 | 7136 | float | RD | Drag indicator: 3. highest value apparent power L3 | VA
Drag indicator (peak indicator) | 17 | 7138 | float | RD | Drag indicator: 3. highest value apparent power sum | VA
Drag indicator (peak indicator) | 17 | 7140 | uint | RD | Drag indicator: point in time [UTC], 3. highest value apparent power L1 | s
Drag indicator (peak indicator) | 17 | 7142 | uint | RD | Drag indicator: point in time [UTC], 3. highest value apparent power L2 | s
Drag indicator (peak indicator) | 17 | 7144 | uint | RD | Drag indicator: point in time [UTC], 3. highest value apparent power L3 | s
Drag indicator (peak indicator) | 17 | 7146 | uint | RD | Drag indicator: point in time [UTC], 3. highest value apparent power sum | s
Drag indicator (peak indicator) | 17 | 7148 | float | RD | Drag indicator: 3. highest value active power L1, consumed | W
Drag indicator (peak indicator) | 17 | 7150 | float | RD | Drag indicator: 3. highest value active power L2, consumed | W
Drag indicator (peak indicator) | 17 | 7152 | float | RD | Drag indicator: 3. highest value active power L3, consumed | W
Drag indicator (peak indicator) | 17 | 7154 | float | RD | Drag indicator: 3. highest value active power sum, consumed | W
Drag indicator (peak indicator) | 17 | 7156 | uint | RD | Drag indicator: point in time [UTC], 3. highest value active power L1, consumed | s
Drag indicator (peak indicator) | 17 | 7158 | uint | RD | Drag indicator: point in time [UTC], 3. highest value active power L2, consumed | s
Drag indicator (peak indicator) | 17 | 7160 | uint | RD | Drag indicator: point in time [UTC], 3. highest value active power L3, consumed | s
Drag indicator (peak indicator) | 17 | 7162 | uint | RD | Drag indicator: point in time [UTC], 3. highest value active power sum, consumed | s
Drag indicator (peak indicator) | 17 | 7164 | float | RD | Drag indicator: 3. highest value active power L1, delivered | W
Drag indicator (peak indicator) | 17 | 7166 | float | RD | Drag indicator: 3. highest value active power L2, delivered | W
Drag indicator (peak indicator) | 17 | 7168 | float | RD | Drag indicator: 3. highest value active power L3, delivered | W
Drag indicator (peak indicator) | 17 | 7170 | float | RD | Drag indicator: 3. highest value active power sum, delivered | W
Drag indicator (peak indicator) | 17 | 7172 | uint | RD | Drag indicator: point in time [UTC], 3. highest value active power L1, delivered | s
Drag indicator (peak indicator) | 17 | 7174 | uint | RD | Drag indicator: point in time [UTC], 3. highest value active power L2, delivered | s
Drag indicator (peak indicator) | 17 | 7176 | uint | RD | Drag indicator: point in time [UTC], 3. highest value active power L3, delivered | s
Drag indicator (peak indicator) | 17 | 7178 | uint | RD | Drag indicator: point in time [UTC], 3. highest value active power sum, delivered | s
Energy values | 20 | 5000 | float | RD | Active Energy L1, consumed | Wh
Energy values | 20 | 5002 | float | RD | Active Energy L2, consumed | Wh
Energy values | 20 | 5004 | float | RD | Active Energy L3, consumed | Wh
Energy values | 20 | 5006 | float | RD | Active Energy sum, consumed | Wh
Energy values | 20 | 5008 | float | RD | Active Energy L1, consumed, HT | Wh
Energy values | 20 | 5010 | float | RD | Active Energy L2, consumed, HT | Wh
Energy values | 20 | 5012 | float | RD | Active Energy L3, consumed, HT | Wh
Energy values | 20 | 5014 | float | RD | Active Energy sum, consumed, HT | Wh
Energy values | 20 | 5016 | float | RD | Active Energy L1, consumed, NT | Wh
Energy values | 20 | 5018 | float | RD | Active Energy L2, consumed, NT | Wh
Energy values | 20 | 5020 | float | RD | Active Energy L3, consumed, NT | Wh
Energy values | 20 | 5022 | float | RD | Active Energy sum, consumed, NT | Wh
Energy values | 20 | 5024 | float | RD | Apparent Energy L1 | VAh
Energy values | 20 | 5026 | float | RD | Apparent Energy L2 | VAh
Energy values | 20 | 5028 | float | RD | Apparent Energy L3 | VAh
Energy values | 20 | 5030 | float | RD | Apparent Energy, total | VAh
Energy values | 20 | 5032 | float | RD | Apparent Energy L1, HT | VAh
Energy values | 20 | 5034 | float | RD | Apparent Energy L1, HT | VAh
Energy values | 20 | 5036 | float | RD | Apparent Energy L3, HT | VAh
Energy values | 20 | 5038 | float | RD | Apparent Energy, total, HT | VAh
Energy values | 20 | 5040 | float | RD | Apparent Energy L1, NT | VAh
Energy values | 20 | 5042 | float | RD | Apparent Energy L2, NT | VAh
Energy values | 20 | 5044 | float | RD | Apparent Energy L3, NT | VAh
Energy values | 20 | 5046 | float | RD | Apparent Energy, total, NT | VAh
Energy values | 20 | 5048 | float | RD | Reactive Energy L1, inductive | varh
Energy values | 20 | 5050 | float | RD | Reactive Energy L2, inductive | varh
Energy values | 20 | 5052 | float | RD | Reactive Energy L3, inductive | varh
Energy values | 20 | 5054 | float | RD | Reactive Energy sum, inductive | varh
Energy values | 20 | 5056 | float | RD | Reactive Energy L1, inductive, HT | varh
Energy values | 20 | 5058 | float | RD | Reactive Energy L2, inductive, HT | varh
Energy values | 20 | 5060 | float | RD | Reactive Energy L3, inductive, HT | varh
Energy values | 20 | 5062 | float | RD | Reactive Energy, total, inductive, HT | varh
Energy values | 20 | 5064 | float | RD | Reactive Energy L1, inductive, NT | varh
Energy values | 20 | 5066 | float | RD | Reactive Energy L2, inductive, NT | varh
Energy values | 20 | 5068 | float | RD | Reactive Energy L3, inductive, NT | varh
Energy values | 20 | 5070 | float | RD | Reactive Energy, total, inductive, NT | varh
Energy values | 20 | 5072 | float | RD | Active Energy L1, delivered | Wh
Energy values | 20 | 5074 | float | RD | Active Energy L2, delivered | Wh
Energy values | 20 | 5076 | float | RD | Active Energy L3, delivered | Wh
Energy values | 20 | 5078 | float | RD | Active Energy sum, delivered | Wh
Energy values | 20 | 5080 | float | RD | Reactive Energy L1, capazitive | varh
Energy values | 20 | 5082 | float | RD | Reactive Energy L2, capazitive | varh
Energy values | 20 | 5084 | float | RD | Reactive Energy L3, capazitive | varh
Energy values | 20 | 5086 | float | RD | Reactive Energy sum, capazitive | varh
Energy values | 20 | 5088 | float | RD | Active Energy sum, without return travel block | Wh
Energy values | 20 | 5090 | float | RD | Reactive Energy sum, without return travel block | varh
Energy values | 20 | 5092 | float | RD | Reactive Energy L1, inductive, consumed | varh
Energy values | 20 | 5094 | float | RD | Reactive Energy L2, inductive, consumed | varh
Energy values | 20 | 5096 | float | RD | Reactive Energy L3, inductive, consumed | varh
Energy values | 20 | 5098 | float | RD | Reactive Energy sum, inductive, consumed | varh
Energy values | 20 | 5100 | float | RD | Reactive Energy L1, capazitive, consumed | varh
Energy values | 20 | 5102 | float | RD | Reactive Energy L2, capazitive, consumed | varh
Energy values | 20 | 5104 | float | RD | Reactive Energy L3, capazitive, consumed | varh
Energy values | 20 | 5106 | float | RD | Reactive Energy sum, capazitive, consumed | varh
Energy values | 20 | 5108 | float | RD | Reactive Energy L1, inductive, delivered | varh
Energy values | 20 | 5110 | float | RD | Reactive Energy L2, inductive, delivered | varh
Energy values | 20 | 5112 | float | RD | Reactive Energy L3, inductive, delivered | varh
Energy values | 20 | 5114 | float | RD | Reactive Energy sum, inductive, delivered | varh
Energy values | 20 | 5116 | float | RD | Reactive Energy L1, capazitive, delivered | varh
Energy values | 20 | 5118 | float | RD | Reactive Energy L2, capazitive, delivered | varh
Energy values | 20 | 5120 | float | RD | Reactive Energy L3, capazitive, delivered | varh
Energy values | 20 | 5122 | float | RD | Reactive Energy sum, capazitive, delivered | varh
Energy values | 20 | 5124 | float | RD | Active Energy (consumed), max. monthly value, jan., even year | Wh
Energy values | 20 | 5126 | float | RD | Active Energy (consumed), max. monthly value, feb., even year | Wh
Energy values | 20 | 5128 | float | RD | Active Energy (consumed), max. monthly value, mar., even year | Wh
Energy values | 20 | 5130 | float | RD | Active Energy (consumed), max. monthly value, apr., even year | Wh
Energy values | 20 | 5132 | float | RD | Active Energy (consumed), max. monthly value, may., even year | Wh
Energy values | 20 | 5134 | float | RD | Active Energy (consumed), max. monthly value, jun., even year | Wh
Energy values | 20 | 5136 | float | RD | Active Energy (consumed), max. monthly value, jul., even year | Wh
Energy values | 20 | 5138 | float | RD | Active Energy (consumed), max. monthly value, aug., even year | Wh
Energy values | 20 | 5140 | float | RD | Active Energy (consumed), max. monthly value, sep., even year | Wh
Energy values | 20 | 5142 | float | RD | Active Energy (consumed), max. monthly value, oct., even year | Wh
Energy values | 20 | 5144 | float | RD | Active Energy (consumed), max. monthly value, nov., even year | Wh
Energy values | 20 | 5146 | float | RD | Active Energy (consumed), max. monthly value, dec., even year | Wh
Energy values | 20 | 5148 | float | RD | Active Energy (consumed), max. monthly value, jan., uneven year | Wh
Energy values | 20 | 5150 | float | RD | Active Energy (consumed), max. monthly value, feb., uneven year | Wh
Energy values | 20 | 5152 | float | RD | Active Energy (consumed), max. monthly value, mar., uneven year | Wh
Energy values | 20 | 5154 | float | RD | Active Energy (consumed), max. monthly value, apr., uneven year | Wh
Energy values | 20 | 5156 | float | RD | Active Energy (consumed), max. monthly value, may., uneven year | Wh
Energy values | 20 | 5158 | float | RD | Active Energy (consumed), max. monthly value, jun., uneven year | Wh
Energy values | 20 | 5160 | float | RD | Active Energy (consumed), max. monthly value, jul., uneven year | Wh
Energy values | 20 | 5162 | float | RD | Active Energy (consumed), max. monthly value, aug., uneven year | Wh
Energy values | 20 | 5164 | float | RD | Active Energy (consumed), max. monthly value, sep., uneven year | Wh
Energy values | 20 | 5166 | float | RD | Active Energy (consumed), max. monthly value, oct., uneven year | Wh
Energy values | 20 | 5168 | float | RD | Active Energy (consumed), max. monthly value, nov., uneven year | Wh
Energy values | 20 | 5170 | float | RD | Active Energy (consumed), max. monthly value, dec., uneven year | Wh
Energy values | 20 | 5172 | float | RD | Apparent Energy, max. monthly value, jan., even year | VAh
Energy values | 20 | 5174 | float | RD | Apparent Energy, max. monthly value, feb., even year | VAh
Energy values | 20 | 5176 | float | RD | Apparent Energy, max. monthly value, mar., even year | VAh
Energy values | 20 | 5178 | float | RD | Apparent Energy, max. monthly value, apr., even year | VAh
Energy values | 20 | 5180 | float | RD | Apparent Energy, max. monthly value, may., even year | VAh
Energy values | 20 | 5182 | float | RD | Apparent Energy, max. monthly value, jun., even year | VAh
Energy values | 20 | 5184 | float | RD | Apparent Energy, max. monthly value, jul., even year | VAh
Energy values | 20 | 5186 | float | RD | Apparent Energy, max. monthly value, aug., even year | VAh
Energy values | 20 | 5188 | float | RD | Apparent Energy, max. monthly value, sep., even year | VAh
Energy values | 20 | 5190 | float | RD | Apparent Energy, max. monthly value, oct., even year | VAh
Energy values | 20 | 5192 | float | RD | Apparent Energy, max. monthly value, nov., even year | VAh
Energy values | 20 | 5194 | float | RD | Apparent Energy, max. monthly value, dec., even year | VAh
Energy values | 20 | 5196 | float | RD | Apparent Energy, max. monthly value, jan., uneven year | VAh
Energy values | 20 | 5198 | float | RD | Apparent Energy, max. monthly value, feb., uneven year | VAh
Energy values | 20 | 5200 | float | RD | Apparent Energy, max. monthly value, mar., uneven year | VAh
Energy values | 20 | 5202 | float | RD | Apparent Energy, max. monthly value, apr., uneven year | VAh
Energy values | 20 | 5204 | float | RD | Apparent Energy, max. monthly value, may., uneven year | VAh
Energy values | 20 | 5206 | float | RD | Apparent Energy, max. monthly value, jun., uneven year | VAh
Energy values | 20 | 5208 | float | RD | Apparent Energy, max. monthly value, jul., uneven year | VAh
Energy values | 20 | 5210 | float | RD | Apparent Energy, max. monthly value, aug., uneven year | VAh
Energy values | 20 | 5212 | float | RD | Apparent Energy, max. monthly value, sep., uneven year | VAh
Energy values | 20 | 5214 | float | RD | Apparent Energy, max. monthly value, oct., uneven year | VAh
Energy values | 20 | 5216 | float | RD | Apparent Energy, max. monthly value, nov., uneven year | VAh
Energy values | 20 | 5218 | float | RD | Apparent Energy, max. monthly value, dec., uneven year | VAh
Energy values | 20 | 5220 | float | RD | Reactive Energy (ind.), max. monthly value, jan., even year | varh
Energy values | 20 | 5222 | float | RD | Reactive Energy (ind.), max. monthly value, feb., even year | varh
Energy values | 20 | 5224 | float | RD | Reactive Energy (ind.), max. monthly value, mar., even year | varh
Energy values | 20 | 5226 | float | RD | Reactive Energy (ind.), max. monthly value, apr., even year | varh
Energy values | 20 | 5228 | float | RD | Reactive Energy (ind.), max. monthly value, may., even year | varh
Energy values | 20 | 5230 | float | RD | Reactive Energy (ind.), max. monthly value, jun., even year | varh
Energy values | 20 | 5232 | float | RD | Reactive Energy (ind.), max. monthly value, jul., even year | varh
Energy values | 20 | 5234 | float | RD | Reactive Energy (ind.), max. monthly value, aug., even year | varh
Energy values | 20 | 5236 | float | RD | Reactive Energy (ind.), max. monthly value, sep., even year | varh
Energy values | 20 | 5238 | float | RD | Reactive Energy (ind.), max. monthly value, oct., even year | varh
Energy values | 20 | 5240 | float | RD | Reactive Energy (ind.), max. monthly value, nov., even year | varh
Energy values | 20 | 5242 | float | RD | Reactive Energy (ind.), max. monthly value, dec., even year | varh
Energy values | 20 | 5244 | float | RD | Reactive Energy (ind.), max. monthly value, jan., uneven year | varh
Energy values | 20 | 5246 | float | RD | Reactive Energy (ind.), max. monthly value, feb., uneven year | varh
Energy values | 20 | 5248 | float | RD | Reactive Energy (ind.), max. monthly value, mar., uneven year | varh
Energy values | 20 | 5250 | float | RD | Reactive Energy (ind.), max. monthly value, apr., uneven year | varh
Energy values | 20 | 5252 | float | RD | Reactive Energy (ind.), max. monthly value, may., uneven year | varh
Energy values | 20 | 5254 | float | RD | Reactive Energy (ind.), max. monthly value, jun., uneven year | varh
Energy values | 20 | 5256 | float | RD | Reactive Energy (ind.), max. monthly value, jul., uneven year | varh
Energy values | 20 | 5258 | float | RD | Reactive Energy (ind.), max. monthly value, aug., uneven year | varh
Energy values | 20 | 5260 | float | RD | Reactive Energy (ind.), max. monthly value, sep., uneven year | varh
Energy values | 20 | 5262 | float | RD | Reactive Energy (ind.), max. monthly value, oct., uneven year | varh
Energy values | 20 | 5264 | float | RD | Reactive Energy (ind.), max. monthly value, nov., uneven year | varh
Energy values | 20 | 5266 | float | RD | Reactive Energy (ind.), max. monthly value, dec., uneven year | varh
Energy values | 20 | 6000 | double | RD/WR | Active Energy L1, consumed | Wh | 0 | 3.403 e+38
Energy values | 20 | 6004 | double | RD/WR | Active Energy L2, consumed | Wh | 0 | 3.403 e+38
Energy values | 20 | 6008 | double | RD/WR | Active Energy L3, consumed | Wh | 0 | 3.403 e+38
Energy values | 20 | 6012 | double | RD/WR | Active Energy sum, consumed | Wh | 0 | 3.403 e+38
Energy values | 20 | 6016 | double | RD/WR | Active Energy L1, consumed, HT | Wh | 0 | 3.403 e+38
Energy values | 20 | 6020 | double | RD/WR | Active Energy L2, consumed, HT | Wh | 0 | 3.403 e+38
Energy values | 20 | 6024 | double | RD/WR | Active Energy L3, consumed, HT | Wh | 0 | 3.403 e+38
Energy values | 20 | 6028 | double | RD/WR | Active Energy sum, consumed, HT | Wh | 0 | 3.403 e+38
Energy values | 20 | 6032 | double | RD/WR | Active Energy L1, consumed, NT | Wh | 0 | 3.403 e+38
Energy values | 20 | 6036 | double | RD/WR | Active Energy L2, consumed, NT | Wh | 0 | 3.403 e+38
Energy values | 20 | 6040 | double | RD/WR | Active Energy L3, consumed, NT | Wh | 0 | 3.403 e+38
Energy values | 20 | 6044 | double | RD/WR | Active Energy sum, consumed, NT | Wh | 0 | 3.403 e+38
Energy values | 20 | 6048 | double | RD/WR | Apparent Energy L1 | VAh | 0 | 3.403 e+38
Energy values | 20 | 6052 | double | RD/WR | Apparent Energy L2 | VAh | 0 | 3.403 e+38
Energy values | 20 | 6056 | double | RD/WR | Apparent Energy L3 | VAh | 0 | 3.403 e+38
Energy values | 20 | 6060 | double | RD/WR | Apparent Energy, total | VAh | 0 | 3.403 e+38
Energy values | 20 | 6064 | double | RD/WR | Apparent Energy L1, HT | VAh | 0 | 3.403 e+38
Energy values | 20 | 6068 | double | RD/WR | Apparent Energy L2, HT | VAh | 0 | 3.403 e+38
Energy values | 20 | 6072 | double | RD/WR | Apparent Energy L3, HT | VAh | 0 | 3.403 e+38
Energy values | 20 | 6076 | double | RD/WR | Apparent Energy, total, HT | VAh | 0 | 3.403 e+38
Energy values | 20 | 6080 | double | RD/WR | Apparent Energy L1, NT | VAh | 0 | 3.403 e+38
Energy values | 20 | 6084 | double | RD/WR | Apparent Energy L2, NT | VAh | 0 | 3.403 e+38
Energy values | 20 | 6088 | double | RD/WR | Apparent Energy L3, NT | VAh | 0 | 3.403 e+38
Energy values | 20 | 6092 | double | RD/WR | Apparent Energy, total, NT | VAh | 0 | 3.403 e+38
Energy values | 20 | 6096 | double | RD/WR | Reactive Energy L1, inductive | varh | 0 | 3.403 e+38
Energy values | 20 | 6100 | double | RD/WR | Reactive Energy L2, inductive | varh | 0 | 3.403 e+38
Energy values | 20 | 6104 | double | RD/WR | Reactive Energy L3, inductive | varh | 0 | 3.403 e+38
Energy values | 20 | 6108 | double | RD/WR | Reactive Energy sum, inductive | varh | 0 | 3.403 e+38
Energy values | 20 | 6112 | double | RD/WR | Reactive Energy L1, inductive, HT | varh | 0 | 3.403 e+38
Energy values | 20 | 6116 | double | RD/WR | Reactive Energy L2, inductive, HT | varh | 0 | 3.403 e+38
Energy values | 20 | 6120 | double | RD/WR | Reactive Energy L3, inductive, HT | varh | 0 | 3.403 e+38
Energy values | 20 | 6124 | double | RD/WR | Reactive Energy, total, inductive, HT | varh | 0 | 3.403 e+38
Energy values | 20 | 6128 | double | RD/WR | Reactive Energy L1, inductive, NT | varh | 0 | 3.403 e+38
Energy values | 20 | 6132 | double | RD/WR | Reactive Energy L2, inductive, NT | varh | 0 | 3.403 e+38
Energy values | 20 | 6136 | double | RD/WR | Reactive Energy L3, inductive, NT | varh | 0 | 3.403 e+38
Energy values | 20 | 6140 | double | RD/WR | Reactive Energy, total, inductive, NT | varh | 0 | 3.403 e+38
Energy values | 20 | 6144 | double | RD/WR | Active Energy, delivered | Wh | 0 | 3.403 e+38
Energy values | 20 | 6148 | double | RD/WR | Active Energy L2, delivered | Wh | 0 | 3.403 e+38
Energy values | 20 | 6152 | double | RD/WR | Active Energy L3, delivered | Wh | 0 | 3.403 e+38
Energy values | 20 | 6156 | double | RD/WR | Active Energy sum, delivered | Wh | 0 | 3.403 e+38
Energy values | 20 | 6160 | double | RD/WR | Reactive Energy L1, capazitive | varh | 0 | 3.403 e+38
Energy values | 20 | 6164 | double | RD/WR | Reactive Energy L2, capazitive | varh | 0 | 3.403 e+38
Energy values | 20 | 6168 | double | RD/WR | Reactive Energy L3, capazitive | varh | 0 | 3.403 e+38
Energy values | 20 | 6172 | double | RD/WR | Reactive Energy sum, capazitive | varh | 0 | 3.403 e+38
Energy values | 20 | 6176 | double | RD/WR | Active Energy sum, without return travel block | Wh | 0 | 3.403 e+38
Energy values | 20 | 6180 | double | RD/WR | Reactive Energy sum, without return travel block | varh | 0 | 3.403 e+38
Energy values | 20 | 6184 | double | RD/WR | Reactive Energy L1, inductive, consumed | varh | 0 | 3.403 e+38
Energy values | 20 | 6188 | double | RD/WR | Reactive Energy L2, inductive, consumed | varh | 0 | 3.403 e+38
Energy values | 20 | 6192 | double | RD/WR | Reactive Energy L3, inductive, consumed | varh | 0 | 3.403 e+38
Energy values | 20 | 6196 | double | RD/WR | Reactive Energy sum, inductive, consumed | varh | 0 | 3.403 e+38
Energy values | 20 | 6200 | double | RD/WR | Reactive Energy L1, capazitive, consumed | varh | 0 | 3.403 e+38
Energy values | 20 | 6204 | double | RD/WR | Reactive Energy L2, capazitive, consumed | varh | 0 | 3.403 e+38
Energy values | 20 | 6208 | double | RD/WR | Reactive Energy L3, capazitive, consumed | varh | 0 | 3.403 e+38
Energy values | 20 | 6212 | double | RD/WR | Reactive Energy sum, capazitive, consumed | varh | 0 | 3.403 e+38
Energy values | 20 | 6216 | double | RD/WR | Reactive Energy L1, inductive, delivered | varh | 0 | 3.403 e+38
Energy values | 20 | 6220 | double | RD/WR | Reactive Energy L2, inductive, delivered | varh | 0 | 3.403 e+38
Energy values | 20 | 6224 | double | RD/WR | Reactive Energy L3, inductive, delivered | varh | 0 | 3.403 e+38
Energy values | 20 | 6228 | double | RD/WR | Reactive Energy sum, inductive, delivered | varh | 0 | 3.403 e+38
Energy values | 20 | 6232 | double | RD/WR | Reactive Energy L1, capazitive, delivered | varh | 0 | 3.403 e+38
Energy values | 20 | 6236 | double | RD/WR | Reactive Energy L2, capazitive, delivered | varh | 0 | 3.403 e+38
Energy values | 20 | 6240 | double | RD/WR | Reactive Energy L3, capazitive, delivered | varh | 0 | 3.403 e+38
Energy values | 20 | 6244 | double | RD/WR | Reactive Energy sum, capazitive, delivered | varh | 0 | 3.403 e+38
Energy values | 20 | 6248 | double | RD | Active Energy (consumed), max. monthly value, jan., even year | Wh
Energy values | 20 | 6252 | double | RD | Active Energy (consumed), max. monthly value, feb., even year | Wh
Energy values | 20 | 6256 | double | RD | Active Energy (consumed), max. monthly value, mar., even year | Wh
Energy values | 20 | 6260 | double | RD | Active Energy (consumed), max. monthly value, apr., even year | Wh
Energy values | 20 | 6264 | double | RD | Active Energy (consumed), max. monthly value, may., even year | Wh
Energy values | 20 | 6268 | double | RD | Active Energy (consumed), max. monthly value, jun., even year | Wh
Energy values | 20 | 6272 | double | RD | Active Energy (consumed), max. monthly value, jul., even year | Wh
Energy values | 20 | 6276 | double | RD | Active Energy (consumed), max. monthly value, aug., even year | Wh
Energy values | 20 | 6280 | double | RD | Active Energy (consumed), max. monthly value, sep., even year | Wh
Energy values | 20 | 6284 | double | RD | Active Energy (consumed), max. monthly value, oct., even year | Wh
Energy values | 20 | 6288 | double | RD | Active Energy (consumed), max. monthly value, nov., even year | Wh
Energy values | 20 | 6292 | double | RD | Active Energy (consumed), max. monthly value, dec., even year | Wh
Energy values | 20 | 6296 | double | RD | Active Energy (consumed), max. monthly value, jan., uneven year | Wh
Energy values | 20 | 6300 | double | RD | Active Energy (consumed), max. monthly value, feb., uneven year | Wh
Energy values | 20 | 6304 | double | RD | Active Energy (consumed), max. monthly value, mar., uneven year | Wh
Energy values | 20 | 6308 | double | RD | Active Energy (consumed), max. monthly value, apr., uneven year | Wh
Energy values | 20 | 6312 | double | RD | Active Energy (consumed), max. monthly value, may., uneven year | Wh
Energy values | 20 | 6316 | double | RD | Active Energy (consumed), max. monthly value, jun., uneven year | Wh
Energy values | 20 | 6320 | double | RD | Active Energy (consumed), max. monthly value, jul., uneven year | Wh
Energy values | 20 | 6324 | double | RD | Active Energy (consumed), max. monthly value, aug., uneven year | Wh
Energy values | 20 | 6328 | double | RD | Active Energy (consumed), max. monthly value, sep., uneven year | Wh
Energy values | 20 | 6332 | double | RD | Active Energy (consumed), max. monthly value, oct., uneven year | Wh
Energy values | 20 | 6336 | double | RD | Active Energy (consumed), max. monthly value, oct., uneven year | Wh
Energy values | 20 | 6340 | double | RD | Active Energy (consumed), max. monthly value, dec., uneven year | Wh
Energy values | 20 | 6344 | double | RD | Apparent Energy, max. monthly value, jan., even year | VAh
Energy values | 20 | 6348 | double | RD | Apparent Energy, max. monthly value, feb., even year | VAh
Energy values | 20 | 6352 | double | RD | Apparent Energy, max. monthly value, mar., even year | VAh
Energy values | 20 | 6356 | double | RD | Apparent Energy, max. monthly value, apr., even year | VAh
Energy values | 20 | 6360 | double | RD | Apparent Energy, max. monthly value, may., even year | VAh
Energy values | 20 | 6364 | double | RD | Apparent Energy, max. monthly value, jun., even year | VAh
Energy values | 20 | 6368 | double | RD | Apparent Energy, max. monthly value, jul., even year | VAh
Energy values | 20 | 6372 | double | RD | Apparent Energy, max. monthly value, aug., even year | VAh
Energy values | 20 | 6376 | double | RD | Apparent Energy, max. monthly value, sep., even year | VAh
Energy values | 20 | 6380 | double | RD | Apparent Energy, max. monthly value, oct., even year | VAh
Energy values | 20 | 6384 | double | RD | Apparent Energy, max. monthly value, nov., even year | VAh
Energy values | 20 | 6388 | double | RD | Apparent Energy, max. monthly value, dec., even year | VAh
Energy values | 20 | 6392 | double | RD | Apparent Energy, max. monthly value, jan., uneven year | VAh
Energy values | 20 | 6396 | double | RD | Apparent Energy, max. monthly value, feb., uneven year | VAh
Energy values | 20 | 6400 | double | RD | Apparent Energy, max. monthly value, mar., uneven year | VAh
Energy values | 20 | 6404 | double | RD | Apparent Energy, max. monthly value, apr., uneven year | VAh
Energy values | 20 | 6408 | double | RD | Apparent Energy, max. monthly value, may., uneven year | VAh
Energy values | 20 | 6412 | double | RD | Apparent Energy, max. monthly value, jun., uneven year | VAh
Energy values | 20 | 6416 | double | RD | Apparent Energy, max. monthly value, jul., uneven year | VAh
Energy values | 20 | 6420 | double | RD | Apparent Energy, max. monthly value, aug., uneven year | VAh
Energy values | 20 | 6424 | double | RD | Apparent Energy, max. monthly value, sep., uneven year | VAh
Energy values | 20 | 6428 | double | RD | Apparent Energy, max. monthly value, oct., uneven year | VAh
Energy values | 20 | 6432 | double | RD | Apparent Energy, max. monthly value, nov., uneven year | VAh
Energy values | 20 | 6436 | double | RD | Apparent Energy, max. monthly value, dec., uneven year | VAh
Energy values | 20 | 15000 | int | RD | Active Energy L1, consumed | Wh
Energy values | 20 | 15002 | int | RD | Active Energy L2, consumed | Wh
Energy values | 20 | 15004 | int | RD | Active Energy L3, consumed | Wh
Energy values | 20 | 15006 | int | RD | Active Energy sum, consumed | Wh
Energy values | 20 | 15008 | int | RD | Active Energy L1, consumed, HT | Wh
Energy values | 20 | 15010 | int | RD | Active Energy L2, consumed, HT | Wh
Energy values | 20 | 15012 | int | RD | Active Energy L3, consumed, HT | Wh
Energy values | 20 | 15014 | int | RD | Active Energy sum, consumed, HT | Wh
Energy values | 20 | 15016 | int | RD | Active Energy L1, consumed, NT | Wh
Energy values | 20 | 15018 | int | RD | Active Energy L2, consumed, NT | Wh
Energy values | 20 | 15020 | int | RD | Active Energy L3, consumed, NT | Wh
Energy values | 20 | 15022 | int | RD | Active Energy sum, consumed, NT | Wh
Energy values | 20 | 15024 | int | RD | Apparent Energy L1 | VAh
Energy values | 20 | 15026 | int | RD | Apparent Energy L2 | VAh
Energy values | 20 | 15028 | int | RD | Apparent Energy L3 | VAh
Energy values | 20 | 15030 | int | RD | Apparent Energy, total | VAh
Energy values | 20 | 15032 | int | RD | Apparent Energy L1, HT | VAh
Energy values | 20 | 15034 | int | RD | Apparent Energy L2, HT | VAh
Energy values | 20 | 15036 | int | RD | Apparent Energy L3, HT | VAh
Energy values | 20 | 15038 | int | RD | Apparent Energy, total, HT | VAh
Energy values | 20 | 15040 | int | RD | Apparent Energy L1, NT | VAh
Energy values | 20 | 15042 | int | RD | Apparent Energy L2, NT | VAh
Energy values | 20 | 15044 | int | RD | Apparent Energy L3, NT | VAh
Energy values | 20 | 15046 | int | RD | Apparent Energy, total, NT | VAh
Energy values | 20 | 15048 | int | RD | Reactive Energy L1, inductive | varh
Energy values | 20 | 15050 | int | RD | Reactive Energy L2, inductive | varh
Energy values | 20 | 15052 | int | RD | Reactive Energy L3, inductive | varh
Energy values | 20 | 15054 | int | RD | Reactive Energy sum, inductive | varh
Energy values | 20 | 15056 | int | RD | Reactive Energy L1, inductive, HT | varh
Energy values | 20 | 15058 | int | RD | Reactive Energy L2, inductive, HT | varh
Energy values | 20 | 15060 | int | RD | Reactive Energy L3, inductive, HT | varh
Energy values | 20 | 15062 | int | RD | Reactive Energy, total, inductive, HT | varh
Energy values | 20 | 15064 | int | RD | Reactive Energy L1, inductive, NT | varh
Energy values | 20 | 15066 | int | RD | Reactive Energy L2, inductive, NT | varh
Energy values | 20 | 15068 | int | RD | Reactive Energy L3, inductive, NT | varh
Energy values | 20 | 15070 | int | RD | Reactive Energy, total, inductive, NT | varh
Energy values | 20 | 15072 | int | RD | Active Energy L1, delivered | Wh
Energy values | 20 | 15074 | int | RD | Active Energy L2, delivered | Wh
Energy values | 20 | 15076 | int | RD | Active Energy L3, delivered | Wh
Energy values | 20 | 15078 | int | RD | Active Energy sum, delivered | Wh
Energy values | 20 | 15080 | int | RD | Reactive Energy L1, capazitive | varh
Energy values | 20 | 15082 | int | RD | Reactive Energy L2, capazitive | varh
Energy values | 20 | 15084 | int | RD | Reactive Energy L3, capazitive | varh
Energy values | 20 | 15086 | int | RD | Reactive Energy sum, capazitive | varh
Energy values | 20 | 15088 | int | RD | Active Energy sum, without return travel block | Wh
Energy values | 20 | 15090 | int | RD | Reactive Energy sum, without return travel block | varh
Energy values | 20 | 15092 | int | RD | Reactive Energy L1, inductive, consumed | varh
Energy values | 20 | 15094 | int | RD | Reactive Energy L2, inductive, consumed | varh
Energy values | 20 | 15096 | int | RD | Reactive Energy L3, inductive, consumed | varh
Energy values | 20 | 15098 | int | RD | Reactive Energy sum, inductive, consumed | varh
Energy values | 20 | 15100 | int | RD | Reactive Energy L1, capazitive, consumed | varh
Energy values | 20 | 15102 | int | RD | Reactive Energy L2, capazitive, consumed | varh
Energy values | 20 | 15104 | int | RD | Reactive Energy L3, capazitive, consumed | varh
Energy values | 20 | 15106 | int | RD | Reactive Energy sum, capazitive, consumed | varh
Energy values | 20 | 15108 | int | RD | Reactive Energy L1, inductive, delivered | varh
Energy values | 20 | 15110 | int | RD | Reactive Energy L2, inductive, delivered | varh
Energy values | 20 | 15112 | int | RD | Reactive Energy L3, inductive, delivered | varh
Energy values | 20 | 15114 | int | RD | Reactive Energy sum, inductive, delivered | varh
Energy values | 20 | 15116 | int | RD | Reactive Energy L1, capazitive, delivered | varh
Energy values | 20 | 15118 | int | RD | Reactive Energy L2, capazitive, delivered | varh
Energy values | 20 | 15120 | int | RD | Reactive Energy L3, capazitive, delivered | varh
Energy values | 20 | 15122 | int | RD | Reactive Energy sum, capazitive, delivered | varh
Energy values | 20 | 15124 | int | RD | Active Energy (consumed), max. monthly value, jan., even year | Wh
Energy values | 20 | 15126 | int | RD | Active Energy (consumed), max. monthly value, feb., even year | Wh
Energy values | 20 | 15128 | int | RD | Active Energy (consumed), max. monthly value, mar., even year | Wh
Energy values | 20 | 15130 | int | RD | Active Energy (consumed), max. monthly value, apr., even year | Wh
Energy values | 20 | 15132 | int | RD | Active Energy (consumed), max. monthly value, may., even year | Wh
Energy values | 20 | 15134 | int | RD | Active Energy (consumed), max. monthly value, jun., even year | Wh
Energy values | 20 | 15136 | int | RD | Active Energy (consumed), max. monthly value, jul., even year | Wh
Energy values | 20 | 15138 | int | RD | Active Energy (consumed), max. monthly value, aug., even year | Wh
Energy values | 20 | 15140 | int | RD | Active Energy (consumed), max. monthly value, sep., even year | Wh
Energy values | 20 | 15142 | int | RD | Active Energy (consumed), max. monthly value, oct., even year | Wh
Energy values | 20 | 15144 | int | RD | Active Energy (consumed), max. monthly value, nov., even year | Wh
Energy values | 20 | 15146 | int | RD | Active Energy (consumed), max. monthly value, dec., even year | Wh
Energy values | 20 | 15148 | int | RD | Active Energy (consumed), max. monthly value, jan., uneven year | Wh
Energy values | 20 | 15150 | int | RD | Active Energy (consumed), max. monthly value, feb., uneven year | Wh
Energy values | 20 | 15152 | int | RD | Active Energy (consumed), max. monthly value, mar., uneven year | Wh
Energy values | 20 | 15154 | int | RD | Active Energy (consumed), max. monthly value, apr., uneven year | Wh
Energy values | 20 | 15156 | int | RD | Active Energy (consumed), max. monthly value, may., uneven year | Wh
Energy values | 20 | 15158 | int | RD | Active Energy (consumed), max. monthly value, jun., uneven year | Wh
Energy values | 20 | 15160 | int | RD | Active Energy (consumed), max. monthly value, jul., uneven year | Wh
Energy values | 20 | 15162 | int | RD | Active Energy (consumed), max. monthly value, aug., uneven year | Wh
Energy values | 20 | 15164 | int | RD | Active Energy (consumed), max. monthly value, sep., uneven year | Wh
Energy values | 20 | 15166 | int | RD | Active Energy (consumed), max. monthly value, oct., uneven year | Wh
Energy values | 20 | 15168 | int | RD | Active Energy (consumed), max. monthly value, nov., uneven year | Wh
Energy values | 20 | 15170 | int | RD | Active Energy (consumed), max. monthly value, dec., uneven year | Wh
Energy values | 20 | 15192 | int | RD | Apparent Energy, max. monthly value, jan., even year | VAh
Energy values | 20 | 15194 | int | RD | Apparent Energy, max. monthly value, feb., even year | VAh
Energy values | 20 | 15196 | int | RD | Apparent Energy, max. monthly value, mar., even year | VAh
Energy values | 20 | 15198 | int | RD | Apparent Energy, max. monthly value, apr., even year | VAh
Energy values | 20 | 15200 | int | RD | Apparent Energy, max. monthly value, may., even year | VAh
Energy values | 20 | 15202 | int | RD | Apparent Energy, max. monthly value, jun., even year | VAh
Energy values | 20 | 15204 | int | RD | Apparent Energy, max. monthly value, jul., even year | VAh
Energy values | 20 | 15206 | int | RD | Apparent Energy, max. monthly value, aug., even year | VAh
Energy values | 20 | 15208 | int | RD | Apparent Energy, max. monthly value, sep., even year | VAh
Energy values | 20 | 15210 | int | RD | Apparent Energy, max. monthly value, oct., even year | VAh
Energy values | 20 | 15212 | int | RD | Apparent Energy, max. monthly value, nov., even year | VAh
Energy values | 20 | 15214 | int | RD | Apparent Energy, max. monthly value, dec., even year | VAh
Energy values | 20 | 15216 | int | RD | Apparent Energy, max. monthly value, jan., uneven year | VAh
Energy values | 20 | 15218 | int | RD | Apparent Energy, max. monthly value, feb., uneven year | VAh
Energy values | 20 | 15220 | int | RD | Apparent Energy, max. monthly value, mar., uneven year | VAh
Energy values | 20 | 15222 | int | RD | Apparent Energy, max. monthly value, apr., uneven year | VAh
Energy values | 20 | 15224 | int | RD | Apparent Energy, max. monthly value, may., uneven year | VAh
Energy values | 20 | 15226 | int | RD | Apparent Energy, max. monthly value, jun., uneven year | VAh
Energy values | 20 | 15228 | int | RD | Apparent Energy, max. monthly value, jul., uneven year | VAh
Energy values | 20 | 15230 | int | RD | Apparent Energy, max. monthly value, aug., uneven year | VAh
Energy values | 20 | 15232 | int | RD | Apparent Energy, max. monthly value, sep., uneven year | VAh
Energy values | 20 | 15234 | int | RD | Apparent Energy, max. monthly value, oct., uneven year | VAh
Energy values | 20 | 15236 | int | RD | Apparent Energy, max. monthly value, nov., uneven year | VAh
Energy values | 20 | 15238 | int | RD | Apparent Energy, max. monthly value, dec., uneven year | VAh
Energy values | 20 | 15240 | int | RD | Reactive Energy (ind.), max. monthly value, jan., even year | varh
Energy values | 20 | 15242 | int | RD | Reactive Energy (ind.), max. monthly value, feb., even year | varh
Energy values | 20 | 15244 | int | RD | Reactive Energy (ind.), max. monthly value, mar., even year | varh
Energy values | 20 | 15246 | int | RD | Reactive Energy (ind.), max. monthly value, apr., even year | varh
Energy values | 20 | 15248 | int | RD | Reactive Energy (ind.), max. monthly value, may., even year | varh
Energy values | 20 | 15250 | int | RD | Reactive Energy (ind.), max. monthly value, jun., even year | varh
Energy values | 20 | 15252 | int | RD | Reactive Energy (ind.), max. monthly value, jul., even year | varh
Energy values | 20 | 15254 | int | RD | Reactive Energy (ind.), max. monthly value, aug., even year | varh
Energy values | 20 | 15256 | int | RD | Reactive Energy (ind.), max. monthly value, sep., even year | varh
Energy values | 20 | 15258 | int | RD | Reactive Energy (ind.), max. monthly value, oct., even year | varh
Energy values | 20 | 15260 | int | RD | Reactive Energy (ind.), max. monthly value, nov., even year | varh
Energy values | 20 | 15262 | int | RD | Reactive Energy (ind.), max. monthly value, dec., even year | varh
Energy values | 20 | 15264 | int | RD | Reactive Energy (ind.), max. monthly value, jan., uneven year | varh
Energy values | 20 | 15266 | int | RD | Reactive Energy (ind.), max. monthly value, feb., uneven year | varh
Energy values | 20 | 15268 | int | RD | Reactive Energy (ind.), max. monthly value, mar., uneven year | varh
Energy values | 20 | 15270 | int | RD | Reactive Energy (ind.), max. monthly value, apr., uneven year | varh
Energy values | 20 | 15272 | int | RD | Reactive Energy (ind.), max. monthly value, may., uneven year | varh
Energy values | 20 | 15274 | int | RD | Reactive Energy (ind.), max. monthly value, jun., uneven year | varh
Energy values | 20 | 15276 | int | RD | Reactive Energy (ind.), max. monthly value, jul., uneven year | varh
Energy values | 20 | 15278 | int | RD | Reactive Energy (ind.), max. monthly value, aug., uneven year | varh
Energy values | 20 | 15280 | int | RD | Reactive Energy (ind.), max. monthly value, sep., uneven year | varh
Energy values | 20 | 15282 | int | RD | Reactive Energy (ind.), max. monthly value, oct., uneven year | varh
Energy values | 20 | 15284 | int | RD | Reactive Energy (ind.), max. monthly value, nov., uneven year | varh
Energy values | 20 | 15286 | int | RD | Reactive Energy (ind.), max. monthly value, dec., uneven year | varh
Digital inputs/outputs | 25 | 806 | short | RD/WR | Trigger a power quality event by 806=1 |  | 0 | 1
Digital inputs/outputs | 25 | 30046 | short | RD/WR | Function of digital input 1: 0 = S0 input (pulse counter) 1 = Tariff switch HT/NT 5 = Event trigger (PQ series only) - Rising edge 6 =Event trigger (PQ series only) - Falling Flank 7 = Event trigger (PQ series only) - Alternating flank |  | 0 | 7
Digital inputs/outputs | 25 | 30047 | short | RD/WR | Function of digital input 2: 0 = S0 input (pulse counter) 1 = Clock sync - minutes 3 = Clock sync - hours 5 = Event trigger (PQ series only) - Rising edge 6 = Event trigger (PQ series only) - Falling flank 7 = Event trigger (PQ series only) - Alternating flank
Digital inputs/outputs | 25 | 30048 | short | RD/WR | Function of digital input 3: 0 = S0 input (pulse counter) 4 = Drag indicator synchronisation 5 = Event triger (PQ series only) - Rising edge 6 = Event trigger (PQ series only) - Falling flank 7 = Event trigger - Alternating flank |  | 0 | 7
Digital inputs/outputs | 25 | 30400 | short | RD | Digital I/O: status digital Input 1
Digital inputs/outputs | 25 | 30401 | short | RD | Digital I/O: status digital Input 2
Digital inputs/outputs | 25 | 30402 | short | RD | Digital I/O: status digital Input 3
Digital inputs/outputs | 25 | 30406 | short | RD | Digital I/O: status digital Output 1
Digital inputs/outputs | 25 | 30407 | short | RD | Digital I/O: status digital Output 2
Digital inputs/outputs | 25 | 30408 | short | RD | Digital I/O: status digital Output 3
Digital inputs/outputs | 25 | 30409 | short | RD/WR | Digital I/O: setting output 1 |  | 0 | 1
Digital inputs/outputs | 25 | 30410 | short | RD/WR | Digital I/O: setting output 2 |  | 0 | 1
Digital inputs/outputs | 25 | 30411 | short | RD/WR | Digital I/O: setting output 3 |  | 0 | 1
Digital inputs/outputs | 25 | 30412 | float | RD | Digital I/O: power values S0 input 1
Digital inputs/outputs | 25 | 30414 | float | RD | Digital I/O: power values S0 input 2
Digital inputs/outputs | 25 | 30416 | float | RD | Digital I/O: power values S0 input 3
Digital inputs/outputs | 25 | 30418 | long64 | RD/WR | Digital I/O: pulse counter, input 1 |  | 0 | 3.403 e+38
Digital inputs/outputs | 25 | 30422 | long64 | RD/WR | Digital I/O: pulse counter, input 2 |  | 0 | 3.403 e+38
Digital inputs/outputs | 25 | 30426 | long64 | RD/WR | Digital I/O: pulse counter, input 3 |  | 0 | 3.403 e+38
Digital inputs/outputs | 25 | 30430 | int | RD | Digital I/O: pulse counter, input 1
Digital inputs/outputs | 25 | 30432 | int | RD | Digital I/O: pulse counter, input 2
Digital inputs/outputs | 25 | 30434 | int | RD | Digital I/O: pulse counter, input 3
Digital inputs/outputs | 25 | 30436 | double | RD | Digital I/O: pulse count x scaling, input 1
Digital inputs/outputs | 25 | 30440 | double | RD | Digital I/O: pulse count x scaling, input 2
Digital inputs/outputs | 25 | 30444 | double | RD | Digital I/O: pulse count x scaling, input 3
Digital inputs/outputs | 25 | 30448 | float | RD | Digital I/O: pulse count x scaling, input 1
Digital inputs/outputs | 25 | 30450 | float | RD | Digital I/O: pulse count x scaling, input 2
Digital inputs/outputs | 25 | 30452 | float | RD | Digital I/O: pulse count x scaling, input 3
Digital inputs/outputs | 25 | 30565 | long64 | RD | Digital I/O: UTC timestamp, event 1, input 1 | s
Digital inputs/outputs | 25 | 30569 | long64 | RD | Digital I/O: UTC timestamp, event 1, input 2 | s
Digital inputs/outputs | 25 | 30573 | long64 | RD | Digital I/O: UTC timestamp, event 1, input 3 | s
Digital inputs/outputs | 25 | 30577 | short | RD | Digital I/O: status, event 1, input 1 (0=off, 1=on)
Digital inputs/outputs | 25 | 30578 | short | RD | Digital I/O: status, event 1, input 2 (0=off, 1=on)
Digital inputs/outputs | 25 | 30579 | short | RD | Digital I/O: status, event 1, input 3 (0=off, 1=on)
Digital inputs/outputs | 25 | 30580 | long64 | RD | Digital I/O: UTC timestamp, event 2, input 1 | s
Digital inputs/outputs | 25 | 30584 | long64 | RD | Digital I/O: UTC timestamp, event 2, input 2 | s
Digital inputs/outputs | 25 | 30588 | long64 | RD | Digital I/O: UTC timestamp, event 2, input 3 | s
Digital inputs/outputs | 25 | 30592 | short | RD | Digital I/O: status, event 2, input 1 (0=off, 1=on)
Digital inputs/outputs | 25 | 30593 | short | RD | Digital I/O: status, event 2, input 2 (0=off, 1=on)
Digital inputs/outputs | 25 | 30594 | short | RD | Digital I/O: status, event 2, input 3 (0=off, 1=on)
Digital inputs/outputs | 25 | 30595 | long64 | RD | Digital I/O: UTC timestamp, event 3, input 1 | s
Digital inputs/outputs | 25 | 30599 | long64 | RD | Digital I/O: UTC timestamp, event 3, input 2 | s
Digital inputs/outputs | 25 | 30603 | long64 | RD | Digital I/O: UTC timestamp, event 3, input 3 | s
Digital inputs/outputs | 25 | 30607 | short | RD | Digital I/O: status, event 3, input 1 (0=off, 1=on)
Digital inputs/outputs | 25 | 30608 | short | RD | Digital I/O: status, event 3, input 2 (0=off, 1=on)
Digital inputs/outputs | 25 | 30609 | short | RD | Digital I/O: status, event 3, input 3 (0=off, 1=on)
Digital inputs/outputs | 25 | 30610 | long64 | RD | Digital I/O: UTC timestamp, event 4, input 1 | s
Digital inputs/outputs | 25 | 30614 | long64 | RD | Digital I/O: UTC timestamp, event 4, input 2 | s
Digital inputs/outputs | 25 | 30618 | long64 | RD | Digital I/O: UTC timestamp, event 4, input 3 | s
Digital inputs/outputs | 25 | 30622 | short | RD | Digital I/O: status, event 4, input 1 (0=off, 1=on)
Digital inputs/outputs | 25 | 30623 | short | RD | Digital I/O: status, event 4, input 2 (0=off, 1=on)
Digital inputs/outputs | 25 | 30624 | short | RD | Digital I/O: status, event 4, input 3 (0=off, 1=on)
Digital inputs/outputs | 25 | 30625 | long64 | RD | Digital I/O: UTC timestamp, event 5, input 1 | s
Digital inputs/outputs | 25 | 30629 | long64 | RD | Digital I/O: UTC timestamp, event 5, input 2 | s
Digital inputs/outputs | 25 | 30633 | long64 | RD | Digital I/O: UTC timestamp, event 5, input 3 | s
Digital inputs/outputs | 25 | 30637 | short | RD | Digital I/O: status, event 5, input 1 (0=off, 1=on)
Digital inputs/outputs | 25 | 30638 | short | RD | Digital I/O: status, event 5, input 2 (0=off, 1=on)
Digital inputs/outputs | 25 | 30639 | short | RD | Digital I/O: status, event 5, input 3 (0=off, 1=on)
Digital inputs/outputs | 25 | 30640 | long64 | RD | Digital I/O: UTC timestamp, event 6, input 1 | s
Digital inputs/outputs | 25 | 30644 | long64 | RD | Digital I/O: UTC timestamp, event 6, input 2 | s
Digital inputs/outputs | 25 | 30648 | long64 | RD | Digital I/O: UTC timestamp, event 6, input 3 | s
Digital inputs/outputs | 25 | 30652 | short | RD | Digital I/O: status, event 6, input 1 (0=off, 1=on)
Digital inputs/outputs | 25 | 30653 | short | RD | Digital I/O: status, event 6, input 2 (0=off, 1=on)
Digital inputs/outputs | 25 | 30654 | short | RD | Digital I/O: status, event 6, input 3 (0=off, 1=on)
Digital inputs/outputs | 25 | 30655 | long64 | RD | Digital I/O: UTC timestamp, event 7, input 1 | s
Digital inputs/outputs | 25 | 30659 | long64 | RD | Digital I/O: UTC timestamp, event 7, input 2 | s
Digital inputs/outputs | 25 | 30663 | long64 | RD | Digital I/O: UTC timestamp, event 7, input 3 | s
Digital inputs/outputs | 25 | 30667 | short | RD | Digital I/O: status, event 7, input 1 (0=off, 1=on)
Digital inputs/outputs | 25 | 30668 | short | RD | Digital I/O: status, event 7, input 2 (0=off, 1=on)
Digital inputs/outputs | 25 | 30669 | short | RD | Digital I/O: status, event 7, input 3 (0=off, 1=on)
Digital inputs/outputs | 25 | 30670 | long64 | RD | Digital I/O: UTC timestamp, event 8, input 1 | s
Digital inputs/outputs | 25 | 30674 | long64 | RD | Digital I/O: UTC timestamp, event 8, input 2 | s
Digital inputs/outputs | 25 | 30678 | long64 | RD | Digital I/O: UTC timestamp, event 8, input 3 | s
Digital inputs/outputs | 25 | 30682 | short | RD | Digital I/O: status, event 8, input 1 (0=off, 1=on)
Digital inputs/outputs | 25 | 30683 | short | RD | Digital I/O: status, event 8, input 2 (0=off, 1=on)
Digital inputs/outputs | 25 | 30684 | short | RD | Digital I/O: status, event 8, input 3 (0=off, 1=on)
Digital inputs/outputs | 25 | 30685 | long64 | RD | Digital I/O: UTC timestamp, event 9, input 1 | s
Digital inputs/outputs | 25 | 30689 | long64 | RD | Digital I/O: UTC timestamp, event 9, input 2 | s
Digital inputs/outputs | 25 | 30693 | long64 | RD | Digital I/O: UTC timestamp, event 9, input 3 | s
Digital inputs/outputs | 25 | 30697 | short | RD | Digital I/O: status, event 9, input 1 (0=off, 1=on)
Digital inputs/outputs | 25 | 30698 | short | RD | Digital I/O: status, event 9, input 2 (0=off, 1=on)
Digital inputs/outputs | 25 | 30699 | short | RD | Digital I/O: status, event 9, input 3 (0=off, 1=on)
Digital inputs/outputs | 25 | 30700 | long64 | RD | Digital I/O: UTC timestamp, event 10, input 1 | s
Digital inputs/outputs | 25 | 30704 | long64 | RD | Digital I/O: UTC timestamp, event 10, input 2 | s
Digital inputs/outputs | 25 | 30708 | long64 | RD | Digital I/O: UTC timestamp, event 10, input 3 | s
Digital inputs/outputs | 25 | 30712 | short | RD | Digital I/O: status, event 10, input 1 (0=off, 1=on)
Digital inputs/outputs | 25 | 30713 | short | RD | Digital I/O: status, event 10, input 2 (0=off, 1=on)
Digital inputs/outputs | 25 | 30714 | short | RD | Digital I/O: status, event 10, input 3 (0=off, 1=on)
Digital inputs/outputs | 25 | 30715 | long64 | RD | Digital I/O: UTC timestamp, event 11, input 1 | s
Digital inputs/outputs | 25 | 30719 | long64 | RD | Digital I/O: UTC timestamp, event 11, input 2 | s
Digital inputs/outputs | 25 | 30723 | long64 | RD | Digital I/O: UTC timestamp, event 11, input 3 | s
Digital inputs/outputs | 25 | 30727 | short | RD | Digital I/O: status, event 11, input 1 (0=off, 1=on)
Digital inputs/outputs | 25 | 30728 | short | RD | Digital I/O: status, event 11, input 2 (0=off, 1=on)
Digital inputs/outputs | 25 | 30729 | short | RD | Digital I/O: status, event 11, input 3 (0=off, 1=on)
Digital inputs/outputs | 25 | 30730 | long64 | RD | Digital I/O: UTC timestamp, event 12, input 1 | s
Digital inputs/outputs | 25 | 30734 | long64 | RD | Digital I/O: UTC timestamp, event 12, input 2 | s
Digital inputs/outputs | 25 | 30738 | long64 | RD | Digital I/O: UTC timestamp, event 12, input 3 | s
Digital inputs/outputs | 25 | 30742 | short | RD | Digital I/O: status, event 12, input 1 (0=off, 1=on)
Digital inputs/outputs | 25 | 30743 | short | RD | Digital I/O: status, event 12, input 2 (0=off, 1=on)
Digital inputs/outputs | 25 | 30744 | short | RD | Digital I/O: status, event 12, input 3 (0=off, 1=on)
Digital inputs/outputs | 25 | 30745 | long64 | RD | Digital I/O: UTC timestamp, event 13, input 1 | s
Digital inputs/outputs | 25 | 30749 | long64 | RD | Digital I/O: UTC timestamp, event 13, input 2 | s
Digital inputs/outputs | 25 | 30753 | long64 | RD | Digital I/O: UTC timestamp, event 13, input 3 | s
Digital inputs/outputs | 25 | 30757 | short | RD | Digital I/O: status, event 13, input 1 (0=off, 1=on)
Digital inputs/outputs | 25 | 30758 | short | RD | Digital I/O: status, event 13, input 2 (0=off, 1=on)
Digital inputs/outputs | 25 | 30759 | short | RD | Digital I/O: status, event 13, input 3 (0=off, 1=on)
Digital inputs/outputs | 25 | 30760 | long64 | RD | Digital I/O: UTC timestamp, event 14, input 1 | s
Digital inputs/outputs | 25 | 30764 | long64 | RD | Digital I/O: UTC timestamp, event 14, input 2 | s
Digital inputs/outputs | 25 | 30768 | long64 | RD | Digital I/O: UTC timestamp, event 14, input 3 | s
Digital inputs/outputs | 25 | 30772 | short | RD | Digital I/O: status, event 14, input 1 (0=off, 1=on)
Digital inputs/outputs | 25 | 30773 | short | RD | Digital I/O: status, event 14, input 2 (0=off, 1=on)
Digital inputs/outputs | 25 | 30774 | short | RD | Digital I/O: status, event 14, input 3 (0=off, 1=on)
Digital inputs/outputs | 25 | 30775 | long64 | RD | Digital I/O: UTC timestamp, event 15, input 1 | s
Digital inputs/outputs | 25 | 30779 | long64 | RD | Digital I/O: UTC timestamp, event 15, input 2 | s
Digital inputs/outputs | 25 | 30783 | long64 | RD | Digital I/O: UTC timestamp, event 15, input 3 | s
Digital inputs/outputs | 25 | 30787 | short | RD | Digital I/O: status, event 15, input 1 (0=off, 1=on)
Digital inputs/outputs | 25 | 30788 | short | RD | Digital I/O: status, event 15, input 2 (0=off, 1=on)
Digital inputs/outputs | 25 | 30789 | short | RD | Digital I/O: status, event 15, input 3 (0=off, 1=on)
Digital inputs/outputs | 25 | 30790 | long64 | RD | Digital I/O: UTC timestamp, event 16, input 1 | s
Digital inputs/outputs | 25 | 30794 | long64 | RD | Digital I/O: UTC timestamp, event 16, input 2 | s
Digital inputs/outputs | 25 | 30798 | long64 | RD | Digital I/O: UTC timestamp, event 16, input 3 | s
Digital inputs/outputs | 25 | 30802 | short | RD | Digital I/O: status, event 16, input 1 (0=off, 1=on)
Digital inputs/outputs | 25 | 30803 | short | RD | Digital I/O: status, event 16, input 2 (0=off, 1=on)
Digital inputs/outputs | 25 | 30804 | short | RD | Digital I/O: status, event 16, input 3 (0=off, 1=on)
Comparator groups | 30 | 32500 | char | RD | PQ-L series: comparator group 1 comparator A
Comparator groups | 30 | 32501 | char | RD | PQ-L series: comparator group 1 comparator B
Comparator groups | 30 | 32502 | char | RD | PQ-L series: comparator group 1 comparator C
Comparator groups | 30 | 32503 | char | RD | PQ-L series: comparator group 1 comparator D
Comparator groups | 30 | 32504 | char | RD | PQ-L series: comparator group 1 comparator E
Comparator groups | 30 | 32505 | char | RD | PQ-L series: comparator group 1 comparator F
Comparator groups | 30 | 32506 | char | RD | PQ-L series: comparator group 1 comparator G
Comparator groups | 30 | 32507 | char | RD | PQ-L series: comparator group 1 comparator H
Comparator groups | 30 | 32508 | char | RD | PQ-L series: comparator group 1 comparator I
Comparator groups | 30 | 32509 | char | RD | PQ-L series: comparator group 1 comparator J
Comparator groups | 30 | 32510 | char | RD | PQ-L series: comparator group 1 group comparator 1
Comparator groups | 30 | 32511 | char | RD | PQ-L series: comparator group 2 comparator A
Comparator groups | 30 | 32512 | char | RD | PQ-L series: comparator group 2 comparator B
Comparator groups | 30 | 32513 | char | RD | PQ-L series: comparator group 2 comparator C
Comparator groups | 30 | 32514 | char | RD | PQ-L series: comparator group 2 comparator D
Comparator groups | 30 | 32515 | char | RD | PQ-L series: comparator group 2 comparator E
Comparator groups | 30 | 32516 | char | RD | PQ-L series: comparator group 2 comparator F
Comparator groups | 30 | 32517 | char | RD | PQ-L series: comparator group 2 comparator G
Comparator groups | 30 | 32518 | char | RD | PQ-L series: comparator group 2 comparator H
Comparator groups | 30 | 32519 | char | RD | PQ-L series: comparator group 2 comparator I
Comparator groups | 30 | 32520 | char | RD | PQ-L series: comparator group 2 comparator J
Comparator groups | 30 | 32521 | char | RD | PQ-L series: comparator group 2 group comparator 2
Comparator groups | 30 | 32522 | char | RD | PQ-L series: comparator group 3 comparator A
Comparator groups | 30 | 32523 | char | RD | PQ-L series: comparator group 3 comparator B
Comparator groups | 30 | 32524 | char | RD | PQ-L series: comparator group 3 comparator C
Comparator groups | 30 | 32525 | char | RD | PQ-L series: comparator group 3 comparator D
Comparator groups | 30 | 32526 | char | RD | PQ-L series: comparator group 3 comparator E
Comparator groups | 30 | 32527 | char | RD | PQ-L series: comparator group 3 comparator F
Comparator groups | 30 | 32528 | char | RD | PQ-L series: comparator group 3 comparator G
Comparator groups | 30 | 32529 | char | RD | PQ-L series: comparator group 3 comparator H
Comparator groups | 30 | 32530 | char | RD | PQ-L series: comparator group 3 comparator I
Comparator groups | 30 | 32531 | char | RD | PQ-L series: comparator group 3 comparator J
Comparator groups | 30 | 32532 | char | RD | PQ-L series: comparator group 3 group comparator 3
Comparator groups | 30 | 32533 | char | RD | PQ-L series: comparator group 4 comparator A
Comparator groups | 30 | 32534 | char | RD | PQ-L series: comparator group 4 comparator B
Comparator groups | 30 | 32535 | char | RD | PQ-L series: comparator group 4 comparator C
Comparator groups | 30 | 32536 | char | RD | PQ-L series: comparator group 4 comparator D
Comparator groups | 30 | 32537 | char | RD | PQ-L series: comparator group 4 comparator E
Comparator groups | 30 | 32538 | char | RD | PQ-L series: comparator group 4 comparator F
Comparator groups | 30 | 32539 | char | RD | PQ-L series: comparator group 4 comparator G
Comparator groups | 30 | 32540 | char | RD | PQ-L series: comparator group 4 comparator H
Comparator groups | 30 | 32541 | char | RD | PQ-L series: comparator group 4 comparator I
Comparator groups | 30 | 32542 | char | RD | PQ-L series: comparator group 4 comparator J
Comparator groups | 30 | 32543 | char | RD | PQ-L series: comparator group 4 group comparator 4
Comparator groups | 30 | 32544 | char | RD | PQ-L series: comparator group 5 comparator A
Comparator groups | 30 | 32545 | char | RD | PQ-L series: comparator group 5 comparator B
Comparator groups | 30 | 32546 | char | RD | PQ-L series: comparator group 5 comparator C
Comparator groups | 30 | 32547 | char | RD | PQ-L series: comparator group 5 comparator D
Comparator groups | 30 | 32548 | char | RD | PQ-L series: comparator group 5 comparator E
Comparator groups | 30 | 32549 | char | RD | PQ-L series: comparator group 5 comparator F
Comparator groups | 30 | 32550 | char | RD | PQ-L series: comparator group 5 comparator G
Comparator groups | 30 | 32551 | char | RD | PQ-L series: comparator group 5 comparator H
Comparator groups | 30 | 32552 | char | RD | PQ-L series: comparator group 5 comparator I
Comparator groups | 30 | 32553 | char | RD | PQ-L series: comparator group 5 comparator J
Comparator groups | 30 | 32554 | char | RD | PQ-L series: comparator group 5 group comparator 5
Events, read out the last event via Modbus | 31 | 16643 | ushort | RD | Last event phase (consider together with 16644): 0= Phase 1 (U or I), DigIn 1, Modbus event, 1= Phase 2 (U or I), DigIn 2 2= Phase 3 (U or I), DigIn 3 3= Multievent: At least in 2 phases for U and I events. With a frequency event, all 3 phases are always affected. 4= Event I4 5= Event I5 6= Event I6 If the device does not have an event, a 0 is displayed here.
Events, read out the last event via Modbus | 31 | 16644 | short | RD | Event type: -1= No event 0= IMAX_EVENT - Overcurrent 1= UMAX_EVENT - Overvoltage 2= UMIN_EVENT - Undervoltage 3= UOFF_EVENT - Voltage interruption 4= EXT_DIGIN - External event (dig. input) 5= EXT_MODBUS - External event (Modbus) 6= RVC_EVENT - Fast voltage change 7= FREQ_OVER_EVENT - Overfrequency 8= FREQ_UNDER_EVENT - Underfrequency 9= IMAX_RCM_EVENT - Overcurrent event in the analog RCM inputs (only in meters with module)
Events, read out the last event via Modbus | 31 | 16645 | ulong64 | RD | Event start time, UTC timestamp (resolution in ns) 0= no event
Events, read out the last event via Modbus | 31 | 16649 | uint | RD | Event duration (end time - start time in ns), 0= Event type EXT_DIGIN or EXT_MODBUS (external events do not have an end time) 0= No events (with simultaneous „Value -1 = No event“ for the event type)
Events, read out the last event via Modbus | 31 | 16651 | float | RD | Measured value of the event 0= Event type EXT_DIGIN and EXT_MODBUS (external events do not have any measured values) -1= No event
Fourier analysis, measured values | 41 | 1058 | float | RD | Fourier analysis: 1. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 1060 | float | RD | Fourier analysis: 3. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 1062 | float | RD | Fourier analysis: 5. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 1064 | float | RD | Fourier analysis: 7. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 1066 | float | RD | Fourier analysis: 9. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 1068 | float | RD | Fourier analysis: 11. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 1070 | float | RD | Fourier analysis: 13. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 1072 | float | RD | Fourier analysis: 15. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 1074 | float | RD | Fourier analysis: 17. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 1076 | float | RD | Fourier analysis: 19. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 1078 | float | RD | Fourier analysis: 21. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 1080 | float | RD | Fourier analysis: 23. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 1082 | float | RD | Fourier analysis: 25. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 1084 | float | RD | Fourier analysis: 1. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 1086 | float | RD | Fourier analysis: 3. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 1088 | float | RD | Fourier analysis: 5. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 1090 | float | RD | Fourier analysis: 7. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 1092 | float | RD | Fourier analysis: 9. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 1094 | float | RD | Fourier analysis: 11. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 1096 | float | RD | Fourier analysis: 13. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 1098 | float | RD | Fourier analysis: 15. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 1100 | float | RD | Fourier analysis: 17. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 1102 | float | RD | Fourier analysis: 19. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 1104 | float | RD | Fourier analysis: 21. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 1106 | float | RD | Fourier analysis: 23. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 1108 | float | RD | Fourier analysis: 25. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 1110 | float | RD | Fourier analysis: 1. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 1112 | float | RD | Fourier analysis: 3. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 1114 | float | RD | Fourier analysis: 5. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 1116 | float | RD | Fourier analysis: 7. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 1118 | float | RD | Fourier analysis: 9. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 1120 | float | RD | Fourier analysis: 11. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 1122 | float | RD | Fourier analysis: 13. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 1124 | float | RD | Fourier analysis: 15. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 1126 | float | RD | Fourier analysis: 17. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 1128 | float | RD | Fourier analysis: 19. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 1130 | float | RD | Fourier analysis: 21. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 1132 | float | RD | Fourier analysis: 23. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 1134 | float | RD | Fourier analysis: 25. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 1136 | float | RD | Fourier analysis: 1. harmonic current L1 | A
Fourier analysis, measured values | 41 | 1138 | float | RD | Fourier analysis: 3. harmonic current L1 | A
Fourier analysis, measured values | 41 | 1140 | float | RD | Fourier analysis: 5. harmonic current L1 | A
Fourier analysis, measured values | 41 | 1142 | float | RD | Fourier analysis: 7. harmonic current L1 | A
Fourier analysis, measured values | 41 | 1144 | float | RD | Fourier analysis: 9. harmonic current L1 | A
Fourier analysis, measured values | 41 | 1146 | float | RD | Fourier analysis: 11. harmonic current L1 | A
Fourier analysis, measured values | 41 | 1148 | float | RD | Fourier analysis: 13. harmonic current L1 | A
Fourier analysis, measured values | 41 | 1150 | float | RD | Fourier analysis: 15. harmonic current L1 | A
Fourier analysis, measured values | 41 | 1152 | float | RD | Fourier analysis: 17. harmonic current L1 | A
Fourier analysis, measured values | 41 | 1154 | float | RD | Fourier analysis: 19. harmonic current L1 | A
Fourier analysis, measured values | 41 | 1156 | float | RD | Fourier analysis: 21. harmonic current L1 | A
Fourier analysis, measured values | 41 | 1158 | float | RD | Fourier analysis: 23. harmonic current L1 | A
Fourier analysis, measured values | 41 | 1160 | float | RD | Fourier analysis: 25. harmonic current L1 | A
Fourier analysis, measured values | 41 | 1162 | float | RD | Fourier analysis: 1. harmonic current L2 | A
Fourier analysis, measured values | 41 | 1164 | float | RD | Fourier analysis: 3. harmonic current L2 | A
Fourier analysis, measured values | 41 | 1166 | float | RD | Fourier analysis: 5. harmonic current L2 | A
Fourier analysis, measured values | 41 | 1168 | float | RD | Fourier analysis: 7. harmonic current L2 | A
Fourier analysis, measured values | 41 | 1170 | float | RD | Fourier analysis: 9. harmonic current L2 | A
Fourier analysis, measured values | 41 | 1172 | float | RD | Fourier analysis: 11. harmonic current L2 | A
Fourier analysis, measured values | 41 | 1174 | float | RD | Fourier analysis: 13. harmonic current L2 | A
Fourier analysis, measured values | 41 | 1176 | float | RD | Fourier analysis: 15. harmonic current L2 | A
Fourier analysis, measured values | 41 | 1178 | float | RD | Fourier analysis: 17. harmonic current L2 | A
Fourier analysis, measured values | 41 | 1180 | float | RD | Fourier analysis: 19. harmonic current L2 | A
Fourier analysis, measured values | 41 | 1182 | float | RD | Fourier analysis: 21. harmonic current L2 | A
Fourier analysis, measured values | 41 | 1184 | float | RD | Fourier analysis: 23. harmonic current L2 | A
Fourier analysis, measured values | 41 | 1186 | float | RD | Fourier analysis: 25. harmonic current L2 | A
Fourier analysis, measured values | 41 | 1188 | float | RD | Fourier analysis: 1. harmonic current L3 | A
Fourier analysis, measured values | 41 | 1190 | float | RD | Fourier analysis: 3. harmonic current L3 | A
Fourier analysis, measured values | 41 | 1192 | float | RD | Fourier analysis: 5. harmonic current L3 | A
Fourier analysis, measured values | 41 | 1194 | float | RD | Fourier analysis: 7. harmonic current L3 | A
Fourier analysis, measured values | 41 | 1196 | float | RD | Fourier analysis: 9. harmonic current L3 | A
Fourier analysis, measured values | 41 | 1198 | float | RD | Fourier analysis: 11. harmonic current L3 | A
Fourier analysis, measured values | 41 | 1200 | float | RD | Fourier analysis: 13. harmonic current L3 | A
Fourier analysis, measured values | 41 | 1202 | float | RD | Fourier analysis: 15. harmonic current L3 | A
Fourier analysis, measured values | 41 | 1204 | float | RD | Fourier analysis: 17. harmonic current L3 | A
Fourier analysis, measured values | 41 | 1206 | float | RD | Fourier analysis: 19. harmonic current L3 | A
Fourier analysis, measured values | 41 | 1208 | float | RD | Fourier analysis: 21. harmonic current L3 | A
Fourier analysis, measured values | 41 | 1210 | float | RD | Fourier analysis: 23. harmonic current L3 | A
Fourier analysis, measured values | 41 | 1212 | float | RD | Fourier analysis: 25. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8000 | float | RD | Fourier analysis: 1. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8002 | float | RD | Fourier analysis: 2. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8004 | float | RD | Fourier analysis: 3. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8006 | float | RD | Fourier analysis: 4. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8008 | float | RD | Fourier analysis: 5. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8010 | float | RD | Fourier analysis: 6. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8012 | float | RD | Fourier analysis: 7. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8014 | float | RD | Fourier analysis: 8. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8016 | float | RD | Fourier analysis: 9. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8018 | float | RD | Fourier analysis: 10. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8020 | float | RD | Fourier analysis: 11. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8022 | float | RD | Fourier analysis: 12. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8024 | float | RD | Fourier analysis: 13. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8026 | float | RD | Fourier analysis: 14. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8028 | float | RD | Fourier analysis: 15. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8030 | float | RD | Fourier analysis: 16. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8032 | float | RD | Fourier analysis: 17. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8034 | float | RD | Fourier analysis: 18. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8036 | float | RD | Fourier analysis: 19. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8038 | float | RD | Fourier analysis: 20. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8040 | float | RD | Fourier analysis: 21. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8042 | float | RD | Fourier analysis: 22. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8044 | float | RD | Fourier analysis: 23. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8046 | float | RD | Fourier analysis: 24. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8048 | float | RD | Fourier analysis: 25. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8050 | float | RD | Fourier analysis: 26. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8052 | float | RD | Fourier analysis: 27. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8054 | float | RD | Fourier analysis: 28. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8056 | float | RD | Fourier analysis: 29. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8058 | float | RD | Fourier analysis: 30. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8060 | float | RD | Fourier analysis: 31. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8062 | float | RD | Fourier analysis: 32. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8064 | float | RD | Fourier analysis: 33. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8066 | float | RD | Fourier analysis: 34. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8068 | float | RD | Fourier analysis: 35. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8070 | float | RD | Fourier analysis: 36. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8072 | float | RD | Fourier analysis: 37. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8074 | float | RD | Fourier analysis: 38. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8076 | float | RD | Fourier analysis: 39. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8078 | float | RD | Fourier analysis: 40. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 8080 | float | RD | Fourier analysis: 1. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8082 | float | RD | Fourier analysis: 2. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8084 | float | RD | Fourier analysis: 3. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8086 | float | RD | Fourier analysis: 4. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8088 | float | RD | Fourier analysis: 5. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8090 | float | RD | Fourier analysis: 6. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8092 | float | RD | Fourier analysis: 7. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8094 | float | RD | Fourier analysis: 8. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8096 | float | RD | Fourier analysis: 9. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8098 | float | RD | Fourier analysis: 10. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8100 | float | RD | Fourier analysis: 11. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8102 | float | RD | Fourier analysis: 12. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8104 | float | RD | Fourier analysis: 13. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8106 | float | RD | Fourier analysis: 14. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8108 | float | RD | Fourier analysis: 15. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8110 | float | RD | Fourier analysis: 16. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8112 | float | RD | Fourier analysis: 17. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8114 | float | RD | Fourier analysis: 18. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8116 | float | RD | Fourier analysis: 19. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8118 | float | RD | Fourier analysis: 20. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8120 | float | RD | Fourier analysis: 21. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8122 | float | RD | Fourier analysis: 22. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8124 | float | RD | Fourier analysis: 23. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8126 | float | RD | Fourier analysis: 24. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8128 | float | RD | Fourier analysis: 25. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8130 | float | RD | Fourier analysis: 26. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8132 | float | RD | Fourier analysis: 27. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8134 | float | RD | Fourier analysis: 28. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8136 | float | RD | Fourier analysis: 29. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8138 | float | RD | Fourier analysis: 30. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8140 | float | RD | Fourier analysis: 31. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8142 | float | RD | Fourier analysis: 32. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8144 | float | RD | Fourier analysis: 33. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8146 | float | RD | Fourier analysis: 34. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8148 | float | RD | Fourier analysis: 35. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8150 | float | RD | Fourier analysis: 36. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8152 | float | RD | Fourier analysis: 37. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8154 | float | RD | Fourier analysis: 38. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8156 | float | RD | Fourier analysis: 39. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8158 | float | RD | Fourier analysis: 40. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 8160 | float | RD | Fourier analysis: 1. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8162 | float | RD | Fourier analysis: 2. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8164 | float | RD | Fourier analysis: 3. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8166 | float | RD | Fourier analysis: 4. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8168 | float | RD | Fourier analysis: 5. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8170 | float | RD | Fourier analysis: 6. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8172 | float | RD | Fourier analysis: 7. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8174 | float | RD | Fourier analysis: 8. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8176 | float | RD | Fourier analysis: 9. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8178 | float | RD | Fourier analysis: 10. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8180 | float | RD | Fourier analysis: 11. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8182 | float | RD | Fourier analysis: 12. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8184 | float | RD | Fourier analysis: 13. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8186 | float | RD | Fourier analysis: 14. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8188 | float | RD | Fourier analysis: 15. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8190 | float | RD | Fourier analysis: 16. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8192 | float | RD | Fourier analysis: 17. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8194 | float | RD | Fourier analysis: 18. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8196 | float | RD | Fourier analysis: 19. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8198 | float | RD | Fourier analysis: 20. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8200 | float | RD | Fourier analysis: 21. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8202 | float | RD | Fourier analysis: 22. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8204 | float | RD | Fourier analysis: 23. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8206 | float | RD | Fourier analysis: 24. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8208 | float | RD | Fourier analysis: 25. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8210 | float | RD | Fourier analysis: 26. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8212 | float | RD | Fourier analysis: 27. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8214 | float | RD | Fourier analysis: 28. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8216 | float | RD | Fourier analysis: 29. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8218 | float | RD | Fourier analysis: 30. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8220 | float | RD | Fourier analysis: 31. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8222 | float | RD | Fourier analysis: 32. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8224 | float | RD | Fourier analysis: 33. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8226 | float | RD | Fourier analysis: 34. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8228 | float | RD | Fourier analysis: 35. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8230 | float | RD | Fourier analysis: 36. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8232 | float | RD | Fourier analysis: 37. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8234 | float | RD | Fourier analysis: 38. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8236 | float | RD | Fourier analysis: 39. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8238 | float | RD | Fourier analysis: 40. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 8240 | float | RD | Fourier analysis: 1. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8242 | float | RD | Fourier analysis: 2. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8244 | float | RD | Fourier analysis: 3. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8246 | float | RD | Fourier analysis: 4. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8248 | float | RD | Fourier analysis: 5. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8250 | float | RD | Fourier analysis: 6. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8252 | float | RD | Fourier analysis: 7. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8254 | float | RD | Fourier analysis: 8. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8256 | float | RD | Fourier analysis: 9. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8258 | float | RD | Fourier analysis: 10. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8260 | float | RD | Fourier analysis: 11. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8262 | float | RD | Fourier analysis: 12. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8264 | float | RD | Fourier analysis: 13. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8266 | float | RD | Fourier analysis: 14. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8268 | float | RD | Fourier analysis: 15. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8270 | float | RD | Fourier analysis: 16. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8272 | float | RD | Fourier analysis: 17. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8274 | float | RD | Fourier analysis: 18. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8276 | float | RD | Fourier analysis: 19. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8278 | float | RD | Fourier analysis: 20. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8280 | float | RD | Fourier analysis: 21. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8282 | float | RD | Fourier analysis: 22. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8284 | float | RD | Fourier analysis: 23. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8286 | float | RD | Fourier analysis: 24. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8288 | float | RD | Fourier analysis: 25. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8290 | float | RD | Fourier analysis: 26. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8292 | float | RD | Fourier analysis: 27. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8294 | float | RD | Fourier analysis: 28. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8296 | float | RD | Fourier analysis: 29. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8298 | float | RD | Fourier analysis: 30. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8300 | float | RD | Fourier analysis: 31. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8302 | float | RD | Fourier analysis: 32. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8304 | float | RD | Fourier analysis: 33. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8306 | float | RD | Fourier analysis: 34. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8308 | float | RD | Fourier analysis: 35. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8310 | float | RD | Fourier analysis: 36. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8312 | float | RD | Fourier analysis: 37. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8314 | float | RD | Fourier analysis: 38. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8316 | float | RD | Fourier analysis: 39. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8318 | float | RD | Fourier analysis: 40. harmonic current L1 | A
Fourier analysis, measured values | 41 | 8320 | float | RD | Fourier analysis: 1. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8322 | float | RD | Fourier analysis: 2. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8324 | float | RD | Fourier analysis: 3. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8326 | float | RD | Fourier analysis: 4. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8328 | float | RD | Fourier analysis: 5. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8330 | float | RD | Fourier analysis: 6. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8332 | float | RD | Fourier analysis: 7. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8334 | float | RD | Fourier analysis: 8. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8336 | float | RD | Fourier analysis: 9. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8338 | float | RD | Fourier analysis: 10. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8340 | float | RD | Fourier analysis: 11. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8342 | float | RD | Fourier analysis: 12. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8344 | float | RD | Fourier analysis: 13. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8346 | float | RD | Fourier analysis: 14. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8348 | float | RD | Fourier analysis: 15. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8350 | float | RD | Fourier analysis: 16. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8352 | float | RD | Fourier analysis: 17. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8354 | float | RD | Fourier analysis: 18. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8356 | float | RD | Fourier analysis: 19. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8358 | float | RD | Fourier analysis: 20. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8360 | float | RD | Fourier analysis: 21. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8362 | float | RD | Fourier analysis: 22. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8364 | float | RD | Fourier analysis: 23. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8366 | float | RD | Fourier analysis: 24. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8368 | float | RD | Fourier analysis: 25. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8370 | float | RD | Fourier analysis: 26. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8372 | float | RD | Fourier analysis: 27. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8374 | float | RD | Fourier analysis: 28. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8376 | float | RD | Fourier analysis: 29. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8378 | float | RD | Fourier analysis: 30. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8380 | float | RD | Fourier analysis: 31. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8382 | float | RD | Fourier analysis: 32. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8384 | float | RD | Fourier analysis: 33. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8386 | float | RD | Fourier analysis: 34. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8388 | float | RD | Fourier analysis: 35. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8390 | float | RD | Fourier analysis: 36. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8392 | float | RD | Fourier analysis: 37. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8394 | float | RD | Fourier analysis: 38. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8396 | float | RD | Fourier analysis: 39. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8398 | float | RD | Fourier analysis: 40. harmonic current L2 | A
Fourier analysis, measured values | 41 | 8400 | float | RD | Fourier analysis: 1. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8402 | float | RD | Fourier analysis: 2. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8404 | float | RD | Fourier analysis: 3. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8406 | float | RD | Fourier analysis: 4. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8408 | float | RD | Fourier analysis: 5. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8410 | float | RD | Fourier analysis: 6. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8412 | float | RD | Fourier analysis: 7. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8414 | float | RD | Fourier analysis: 8. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8416 | float | RD | Fourier analysis: 9. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8418 | float | RD | Fourier analysis: 10. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8420 | float | RD | Fourier analysis: 11. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8422 | float | RD | Fourier analysis: 12. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8424 | float | RD | Fourier analysis: 13. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8426 | float | RD | Fourier analysis: 14. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8428 | float | RD | Fourier analysis: 15. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8430 | float | RD | Fourier analysis: 16. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8432 | float | RD | Fourier analysis: 17. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8434 | float | RD | Fourier analysis: 18. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8436 | float | RD | Fourier analysis: 19. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8438 | float | RD | Fourier analysis: 20. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8440 | float | RD | Fourier analysis: 21. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8442 | float | RD | Fourier analysis: 22. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8444 | float | RD | Fourier analysis: 23. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8446 | float | RD | Fourier analysis: 24. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8448 | float | RD | Fourier analysis: 25. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8450 | float | RD | Fourier analysis: 26. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8452 | float | RD | Fourier analysis: 27. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8454 | float | RD | Fourier analysis: 28. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8456 | float | RD | Fourier analysis: 29. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8458 | float | RD | Fourier analysis: 30. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8460 | float | RD | Fourier analysis: 31. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8462 | float | RD | Fourier analysis: 32. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8464 | float | RD | Fourier analysis: 33. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8466 | float | RD | Fourier analysis: 34. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8468 | float | RD | Fourier analysis: 35. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8470 | float | RD | Fourier analysis: 36. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8472 | float | RD | Fourier analysis: 37. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8474 | float | RD | Fourier analysis: 38. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8476 | float | RD | Fourier analysis: 39. harmonic current L3 | A
Fourier analysis, measured values | 41 | 8478 | float | RD | Fourier analysis: 40. harmonic current L3 | A
Fourier analysis, measured values | 41 | 11029 | short (x10) | RD | Fourier analysis: 1. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 11030 | short (x10) | RD | Fourier analysis: 3. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 11031 | short (x10) | RD | Fourier analysis: 5. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 11032 | short (x10) | RD | Fourier analysis: 7. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 11033 | short (x10) | RD | Fourier analysis: 9. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 11034 | short (x10) | RD | Fourier analysis: 11. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 11035 | short (x10) | RD | Fourier analysis: 13. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 11036 | short (x10) | RD | Fourier analysis: 15. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 11037 | short (x10) | RD | Fourier analysis: 17. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 11038 | short (x10) | RD | Fourier analysis: 19. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 11039 | short (x10) | RD | Fourier analysis: 21. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 11040 | short (x10) | RD | Fourier analysis: 23. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 11041 | short (x10) | RD | Fourier analysis: 25. harmonic voltage L1 | V
Fourier analysis, measured values | 41 | 11042 | short (x10) | RD | Fourier analysis: 1. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 11043 | short (x10) | RD | Fourier analysis: 3. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 11044 | short (x10) | RD | Fourier analysis: 5. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 11045 | short (x10) | RD | Fourier analysis: 7. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 11046 | short (x10) | RD | Fourier analysis: 9. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 11047 | short (x10) | RD | Fourier analysis: 11. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 11048 | short (x10) | RD | Fourier analysis: 13. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 11049 | short (x10) | RD | Fourier analysis: 15. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 11050 | short (x10) | RD | Fourier analysis: 17. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 11051 | short (x10) | RD | Fourier analysis: 19. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 11052 | short (x10) | RD | Fourier analysis: 21. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 11053 | short (x10) | RD | Fourier analysis: 23. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 11054 | short (x10) | RD | Fourier analysis: 25. harmonic voltage L2 | V
Fourier analysis, measured values | 41 | 11055 | short (x10) | RD | Fourier analysis: 1. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 11056 | short (x10) | RD | Fourier analysis: 3. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 11057 | short (x10) | RD | Fourier analysis: 5. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 11058 | short (x10) | RD | Fourier analysis: 7. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 11059 | short (x10) | RD | Fourier analysis: 9. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 11060 | short (x10) | RD | Fourier analysis: 11. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 11061 | short (x10) | RD | Fourier analysis: 13. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 11062 | short (x10) | RD | Fourier analysis: 15. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 11063 | short (x10) | RD | Fourier analysis: 17. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 11064 | short (x10) | RD | Fourier analysis: 19. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 11065 | short (x10) | RD | Fourier analysis: 21. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 11066 | short (x10) | RD | Fourier analysis: 23. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 11067 | short (x10) | RD | Fourier analysis: 25. harmonic voltage L3 | V
Fourier analysis, measured values | 41 | 11068 | short (x10) | RD | Fourier analysis: 1. harmonic current L1 | A
Fourier analysis, measured values | 41 | 11069 | short (x10) | RD | Fourier analysis: 3. harmonic current L1 | A
Fourier analysis, measured values | 41 | 11070 | short (x10) | RD | Fourier analysis: 5. harmonic current L1 | A
Fourier analysis, measured values | 41 | 11071 | short (x10) | RD | Fourier analysis: 7. harmonic current L1 | A
Fourier analysis, measured values | 41 | 11072 | short (x10) | RD | Fourier analysis: 9. harmonic current L1 | A
Fourier analysis, measured values | 41 | 11073 | short (x10) | RD | Fourier analysis: 11. harmonic current L1 | A
Fourier analysis, measured values | 41 | 11074 | short (x10) | RD | Fourier analysis: 13. harmonic current L1 | A
Fourier analysis, measured values | 41 | 11075 | short (x10) | RD | Fourier analysis: 15. harmonic current L1 | A
Fourier analysis, measured values | 41 | 11076 | short (x10) | RD | Fourier analysis: 17. harmonic current L1 | A
Fourier analysis, measured values | 41 | 11077 | short (x10) | RD | Fourier analysis: 19. harmonic current L1 | A
Fourier analysis, measured values | 41 | 11078 | short (x10) | RD | Fourier analysis: 21. harmonic current L1 | A
Fourier analysis, measured values | 41 | 11079 | short (x10) | RD | Fourier analysis: 23. harmonic current L1 | A
Fourier analysis, measured values | 41 | 11080 | short (x10) | RD | Fourier analysis: 25. harmonic current L1 | A
Fourier analysis, measured values | 41 | 11081 | short (x10) | RD | Fourier analysis: 1. harmonic current L2 | A
Fourier analysis, measured values | 41 | 11082 | short (x10) | RD | Fourier analysis: 3. harmonic current L2 | A
Fourier analysis, measured values | 41 | 11083 | short (x10) | RD | Fourier analysis: 5. harmonic current L2 | A
Fourier analysis, measured values | 41 | 11084 | short (x10) | RD | Fourier analysis: 7. harmonic current L2 | A
Fourier analysis, measured values | 41 | 11085 | short (x10) | RD | Fourier analysis: 9. harmonic current L2 | A
Fourier analysis, measured values | 41 | 11086 | short (x10) | RD | Fourier analysis: 11. harmonic current L2 | A
Fourier analysis, measured values | 41 | 11087 | short (x10) | RD | Fourier analysis: 13. harmonic current L2 | A
Fourier analysis, measured values | 41 | 11088 | short (x10) | RD | Fourier analysis: 15. harmonic current L2 | A
Fourier analysis, measured values | 41 | 11089 | short (x10) | RD | Fourier analysis: 17. harmonic current L2 | A
Fourier analysis, measured values | 41 | 11090 | short (x10) | RD | Fourier analysis: 19. harmonic current L2 | A
Fourier analysis, measured values | 41 | 11091 | short (x10) | RD | Fourier analysis: 21. harmonic current L2 | A
Fourier analysis, measured values | 41 | 11092 | short (x10) | RD | Fourier analysis: 23. harmonic current L2 | A
Fourier analysis, measured values | 41 | 11093 | short (x10) | RD | Fourier analysis: 25. harmonic current L2 | A
Fourier analysis, measured values | 41 | 11094 | short (x10) | RD | Fourier analysis: 1. harmonic current L3 | A
Fourier analysis, measured values | 41 | 11095 | short (x10) | RD | Fourier analysis: 3. harmonic current L3 | A
Fourier analysis, measured values | 41 | 11096 | short (x10) | RD | Fourier analysis: 5. harmonic current L3 | A
Fourier analysis, measured values | 41 | 11097 | short (x10) | RD | Fourier analysis: 7. harmonic current L3 | A
Fourier analysis, measured values | 41 | 11098 | short (x10) | RD | Fourier analysis: 9. harmonic current L3 | A
Fourier analysis, measured values | 41 | 11099 | short (x10) | RD | Fourier analysis: 11. harmonic current L3 | A
Fourier analysis, measured values | 41 | 11100 | short (x10) | RD | Fourier analysis: 13. harmonic current L3 | A
Fourier analysis, measured values | 41 | 11101 | short (x10) | RD | Fourier analysis: 15. harmonic current L3 | A
Fourier analysis, measured values | 41 | 11102 | short (x10) | RD | Fourier analysis: 17. harmonic current L3 | A
Fourier analysis, measured values | 41 | 11103 | short (x10) | RD | Fourier analysis: 19. harmonic current L3 | A
Fourier analysis, measured values | 41 | 11104 | short (x10) | RD | Fourier analysis: 21. harmonic current L3 | A
Fourier analysis, measured values | 41 | 11105 | short (x10) | RD | Fourier analysis: 23. harmonic current L3 | A
Fourier analysis, measured values | 41 | 11106 | short (x10) | RD | Fourier analysis: 25. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 3058 | float | RD | Max. value: 1. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 3060 | float | RD | Max. value: 3. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 3062 | float | RD | Max. value: 5. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 3064 | float | RD | Max. value: 7. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 3066 | float | RD | Max. value: 9. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 3068 | float | RD | Max. value: 11. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 3070 | float | RD | Max. value: 13. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 3072 | float | RD | Max. value: 15. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 3074 | float | RD | Max. value: 17. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 3076 | float | RD | Max. value: 19. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 3078 | float | RD | Max. value: 21. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 3080 | float | RD | Max. value: 23. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 3082 | float | RD | Max. value: 25. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 3084 | float | RD | Max. value: 1. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 3086 | float | RD | Max. value: 3. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 3088 | float | RD | Max. value: 5. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 3090 | float | RD | Max. value: 7. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 3092 | float | RD | Max. value: 9. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 3094 | float | RD | Max. value: 11. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 3096 | float | RD | Max. value: 13. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 3098 | float | RD | Max. value: 15. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 3100 | float | RD | Max. value: 17. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 3102 | float | RD | Max. value: 19. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 3104 | float | RD | Max. value: 21. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 3106 | float | RD | Max. value: 23. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 3108 | float | RD | Max. value: 25. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 3110 | float | RD | Max. value: 1. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 3112 | float | RD | Max. value: 3. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 3114 | float | RD | Max. value: 5. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 3116 | float | RD | Max. value: 7. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 3118 | float | RD | Max. value: 9. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 3120 | float | RD | Max. value: 11. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 3122 | float | RD | Max. value: 13. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 3124 | float | RD | Max. value: 15. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 3126 | float | RD | Max. value: 17. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 3128 | float | RD | Max. value: 19. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 3130 | float | RD | Max. value: 21. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 3132 | float | RD | Max. value: 23. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 3134 | float | RD | Max. value: 25. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 3136 | float | RD | Max. value: 1. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 3138 | float | RD | Max. value: 3. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 3140 | float | RD | Max. value: 5. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 3142 | float | RD | Max. value: 7. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 3144 | float | RD | Max. value: 9. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 3146 | float | RD | Max. value: 11. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 3148 | float | RD | Max. value: 13. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 3150 | float | RD | Max. value: 15. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 3152 | float | RD | Max. value: 17. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 3154 | float | RD | Max. value: 19. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 3156 | float | RD | Max. value: 21. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 3158 | float | RD | Max. value: 23. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 3160 | float | RD | Max. value: 25. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 3162 | float | RD | Max. value: 1. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 3164 | float | RD | Max. value: 3. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 3166 | float | RD | Max. value: 5. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 3168 | float | RD | Max. value: 7. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 3170 | float | RD | Max. value: 9. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 3172 | float | RD | Max. value: 11. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 3174 | float | RD | Max. value: 13. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 3176 | float | RD | Max. value: 15. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 3178 | float | RD | Max. value: 17. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 3180 | float | RD | Max. value: 19. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 3182 | float | RD | Max. value: 21. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 3184 | float | RD | Max. value: 23. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 3186 | float | RD | Max. value: 25. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 3188 | float | RD | Max. value: 1. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 3190 | float | RD | Max. value: 3. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 3192 | float | RD | Max. value: 5. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 3194 | float | RD | Max. value: 7. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 3196 | float | RD | Max. value: 9. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 3198 | float | RD | Max. value: 11. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 3200 | float | RD | Max. value: 13. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 3202 | float | RD | Max. value: 15. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 3204 | float | RD | Max. value: 17. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 3206 | float | RD | Max. value: 19. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 3208 | float | RD | Max. value: 21. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 3210 | float | RD | Max. value: 23. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 3212 | float | RD | Max. value: 25. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 8960 | float | RD | Max. value: 1. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 8962 | float | RD | Max. value: 2. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 8964 | float | RD | Max. value: 3. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 8966 | float | RD | Max. value: 4. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 8968 | float | RD | Max. value: 5. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 8970 | float | RD | Max. value: 6. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 8972 | float | RD | Max. value: 7. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 8974 | float | RD | Max. value: 8. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 8976 | float | RD | Max. value: 9. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 8978 | float | RD | Max. value: 10. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 8980 | float | RD | Max. value: 11. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 8982 | float | RD | Max. value: 12. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 8984 | float | RD | Max. value: 13. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 8986 | float | RD | Max. value: 14. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 8988 | float | RD | Max. value: 15. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 8990 | float | RD | Max. value: 16. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 8992 | float | RD | Max. value: 17. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 8994 | float | RD | Max. value: 18. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 8996 | float | RD | Max. value: 19. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 8998 | float | RD | Max. value: 20. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 9000 | float | RD | Max. value: 21. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 9002 | float | RD | Max. value: 22. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 9004 | float | RD | Max. value: 23. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 9006 | float | RD | Max. value: 24. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 9008 | float | RD | Max. value: 25. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 9010 | float | RD | Max. value: 26. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 9012 | float | RD | Max. value: 26. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 9014 | float | RD | Max. value: 28. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 9016 | float | RD | Max. value: 29. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 9018 | float | RD | Max. value: 30. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 9020 | float | RD | Max. value: 31. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 9022 | float | RD | Max. value: 32. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 9024 | float | RD | Max. value: 33. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 9026 | float | RD | Max. value: 34. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 9028 | float | RD | Max. value: 35. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 9030 | float | RD | Max. value: 36. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 9032 | float | RD | Max. value: 37. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 9034 | float | RD | Max. value: 38. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 9036 | float | RD | Max. value: 39. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 9038 | float | RD | Max. value: 40. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 9040 | float | RD | Max. value: 1. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9042 | float | RD | Max. value: 2. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9044 | float | RD | Max. value: 3. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9046 | float | RD | Max. value: 4. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9048 | float | RD | Max. value: 5. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9050 | float | RD | Max. value: 6. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9052 | float | RD | Max. value: 7. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9054 | float | RD | Max. value: 8. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9056 | float | RD | Max. value: 9. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9058 | float | RD | Max. value: 10. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9060 | float | RD | Max. value: 11. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9062 | float | RD | Max. value: 12. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9064 | float | RD | Max. value: 13. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9066 | float | RD | Max. value: 14. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9068 | float | RD | Max. value: 15. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9070 | float | RD | Max. value: 16. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9072 | float | RD | Max. value: 17. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9074 | float | RD | Max. value: 18. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9076 | float | RD | Max. value: 19. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9078 | float | RD | Max. value: 20. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9080 | float | RD | Max. value: 21. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9082 | float | RD | Max. value: 22. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9084 | float | RD | Max. value: 23. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9086 | float | RD | Max. value: 24. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9088 | float | RD | Max. value: 25. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9090 | float | RD | Max. value: 26. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9092 | float | RD | Max. value: 27. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9094 | float | RD | Max. value: 28. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9096 | float | RD | Max. value: 29. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9098 | float | RD | Max. value: 30. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9100 | float | RD | Max. value: 31. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9102 | float | RD | Max. value: 32. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9104 | float | RD | Max. value: 33. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9106 | float | RD | Max. value: 34. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9108 | float | RD | Max. value: 35. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9110 | float | RD | Max. value: 36. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9112 | float | RD | Max. value: 37. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9114 | float | RD | Max. value: 38. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9116 | float | RD | Max. value: 39. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9118 | float | RD | Max. value: 40. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 9120 | float | RD | Max. value: 1. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9122 | float | RD | Max. value: 2. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9124 | float | RD | Max. value: 3. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9126 | float | RD | Max. value: 4. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9128 | float | RD | Max. value: 5. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9130 | float | RD | Max. value: 6. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9132 | float | RD | Max. value: 7. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9134 | float | RD | Max. value: 8. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9136 | float | RD | Max. value: 9. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9138 | float | RD | Max. value: 10. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9140 | float | RD | Max. value: 11. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9142 | float | RD | Max. value: 12. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9144 | float | RD | Max. value: 13. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9146 | float | RD | Max. value: 14. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9148 | float | RD | Max. value: 15. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9150 | float | RD | Max. value: 16. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9152 | float | RD | Max. value: 17. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9154 | float | RD | Max. value: 18. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9156 | float | RD | Max. value: 19. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9158 | float | RD | Max. value: 20. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9160 | float | RD | Max. value: 21. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9162 | float | RD | Max. value: 22. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9164 | float | RD | Max. value: 23. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9166 | float | RD | Max. value: 24. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9168 | float | RD | Max. value: 25. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9170 | float | RD | Max. value: 26. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9172 | float | RD | Max. value: 27. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9174 | float | RD | Max. value: 28. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9176 | float | RD | Max. value: 29. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9178 | float | RD | Max. value: 30. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9180 | float | RD | Max. value: 31. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9182 | float | RD | Max. value: 32. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9184 | float | RD | Max. value: 33. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9186 | float | RD | Max. value: 34. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9188 | float | RD | Max. value: 35. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9190 | float | RD | Max. value: 36. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9192 | float | RD | Max. value: 37. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9194 | float | RD | Max. value: 38. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9196 | float | RD | Max. value: 39. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9198 | float | RD | Max. value: 40. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 9200 | float | RD | Max. value: 1. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9202 | float | RD | Max. value: 2. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9204 | float | RD | Max. value: 3. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9206 | float | RD | Max. value: 4. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9208 | float | RD | Max. value: 5. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9210 | float | RD | Max. value: 6. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9212 | float | RD | Max. value: 7. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9214 | float | RD | Max. value: 8. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9216 | float | RD | Max. value: 9. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9218 | float | RD | Max. value: 10. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9220 | float | RD | Max. value: 11. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9222 | float | RD | Max. value: 12. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9224 | float | RD | Max. value: 13. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9226 | float | RD | Max. value: 14. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9228 | float | RD | Max. value: 15. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9230 | float | RD | Max. value: 16. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9232 | float | RD | Max. value: 17. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9234 | float | RD | Max. value: 18. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9236 | float | RD | Max. value: 19. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9238 | float | RD | Max. value: 20. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9240 | float | RD | Max. value: 21. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9242 | float | RD | Max. value: 22. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9244 | float | RD | Max. value: 23. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9246 | float | RD | Max. value: 24. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9248 | float | RD | Max. value: 25. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9250 | float | RD | Max. value: 26. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9252 | float | RD | Max. value: 27. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9254 | float | RD | Max. value: 28. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9256 | float | RD | Max. value: 29. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9258 | float | RD | Max. value: 30. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9260 | float | RD | Max. value: 31. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9262 | float | RD | Max. value: 32. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9264 | float | RD | Max. value: 33. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9266 | float | RD | Max. value: 34. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9268 | float | RD | Max. value: 35. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9270 | float | RD | Max. value: 36. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9272 | float | RD | Max. value: 37. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9274 | float | RD | Max. value: 38. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9276 | float | RD | Max. value: 39. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9278 | float | RD | Max. value: 40. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 9280 | float | RD | Max. value: 1. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9282 | float | RD | Max. value: 2. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9284 | float | RD | Max. value: 3. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9286 | float | RD | Max. value: 4. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9288 | float | RD | Max. value: 5. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9290 | float | RD | Max. value: 6. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9292 | float | RD | Max. value: 7. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9294 | float | RD | Max. value: 8. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9296 | float | RD | Max. value: 9. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9298 | float | RD | Max. value: 10. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9300 | float | RD | Max. value: 11. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9302 | float | RD | Max. value: 12. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9304 | float | RD | Max. value: 13. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9306 | float | RD | Max. value: 14. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9308 | float | RD | Max. value: 15. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9310 | float | RD | Max. value: 16. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9312 | float | RD | Max. value: 17. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9314 | float | RD | Max. value: 18. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9316 | float | RD | Max. value: 19. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9318 | float | RD | Max. value: 20. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9320 | float | RD | Max. value: 21. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9322 | float | RD | Max. value: 22. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9324 | float | RD | Max. value: 23. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9326 | float | RD | Max. value: 24. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9328 | float | RD | Max. value: 25. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9330 | float | RD | Max. value: 26. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9332 | float | RD | Max. value: 27. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9334 | float | RD | Max. value: 28. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9336 | float | RD | Max. value: 29. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9338 | float | RD | Max. value: 30. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9340 | float | RD | Max. value: 31. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9342 | float | RD | Max. value: 32. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9344 | float | RD | Max. value: 33. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9346 | float | RD | Max. value: 34. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9348 | float | RD | Max. value: 35. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9350 | float | RD | Max. value: 36. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9352 | float | RD | Max. value: 37. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9354 | float | RD | Max. value: 38. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9356 | float | RD | Max. value: 39. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9358 | float | RD | Max. value: 40. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 9360 | float | RD | Max. value: 1. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9362 | float | RD | Max. value: 2. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9364 | float | RD | Max. value: 3. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9366 | float | RD | Max. value: 4. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9368 | float | RD | Max. value: 5. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9370 | float | RD | Max. value: 6. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9372 | float | RD | Max. value: 7. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9374 | float | RD | Max. value: 8. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9376 | float | RD | Max. value: 9. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9378 | float | RD | Max. value: 10. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9380 | float | RD | Max. value: 11. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9382 | float | RD | Max. value: 12. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9384 | float | RD | Max. value: 13. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9386 | float | RD | Max. value: 14. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9388 | float | RD | Max. value: 15. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9390 | float | RD | Max. value: 16. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9392 | float | RD | Max. value: 17. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9394 | float | RD | Max. value: 18. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9396 | float | RD | Max. value: 19. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9398 | float | RD | Max. value: 20. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9400 | float | RD | Max. value: 21. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9402 | float | RD | Max. value: 22. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9404 | float | RD | Max. value: 23. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9406 | float | RD | Max. value: 24. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9408 | float | RD | Max. value: 25. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9410 | float | RD | Max. value: 26. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9412 | float | RD | Max. value: 27. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9414 | float | RD | Max. value: 28. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9416 | float | RD | Max. value: 29. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9418 | float | RD | Max. value: 30. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9420 | float | RD | Max. value: 31. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9422 | float | RD | Max. value: 32. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9424 | float | RD | Max. value: 33. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9426 | float | RD | Max. value: 34. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9428 | float | RD | Max. value: 35. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9430 | float | RD | Max. value: 36. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9432 | float | RD | Max. value: 37. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9434 | float | RD | Max. value: 38. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9436 | float | RD | Max. value: 39. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 9438 | float | RD | Max. value: 40. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 13029 | short (x10) | RD | Max. value: 1. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 13030 | short (x10) | RD | Max. value: 3. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 13031 | short (x10) | RD | Max. value: 5. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 13032 | short (x10) | RD | Max. value: 7. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 13033 | short (x10) | RD | Max. value: 9. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 13034 | short (x10) | RD | Max. value: 11. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 13035 | short (x10) | RD | Max. value: 13. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 13036 | short (x10) | RD | Max. value: 15. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 13037 | short (x10) | RD | Max. value: 17. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 13038 | short (x10) | RD | Max. value: 19. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 13039 | short (x10) | RD | Max. value: 21. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 13040 | short (x10) | RD | Max. value: 23. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 13041 | short (x10) | RD | Max. value: 25. harmonic voltage L1 | V
Maximum values, fourier analysis | 43 | 13042 | short (x10) | RD | Max. value: 1. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 13043 | short (x10) | RD | Max. value: 3. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 13044 | short (x10) | RD | Max. value: 5. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 13045 | short (x10) | RD | Max. value: 7. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 13046 | short (x10) | RD | Max. value: 9. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 13047 | short (x10) | RD | Max. value: 11. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 13048 | short (x10) | RD | Max. value: 13. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 13049 | short (x10) | RD | Max. value: 15. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 13050 | short (x10) | RD | Max. value: 17. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 13051 | short (x10) | RD | Max. value: 19. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 13052 | short (x10) | RD | Max. value: 21. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 13053 | short (x10) | RD | Max. value: 23. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 13054 | short (x10) | RD | Max. value: 25. harmonic voltage L2 | V
Maximum values, fourier analysis | 43 | 13055 | short (x10) | RD | Max. value: 1. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 13056 | short (x10) | RD | Max. value: 3. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 13057 | short (x10) | RD | Max. value: 5. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 13058 | short (x10) | RD | Max. value: 7. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 13059 | short (x10) | RD | Max. value: 9. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 13060 | short (x10) | RD | Max. value: 11. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 13061 | short (x10) | RD | Max. value: 13. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 13062 | short (x10) | RD | Max. value: 15. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 13063 | short (x10) | RD | Max. value: 17. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 13064 | short (x10) | RD | Max. value: 19. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 13065 | short (x10) | RD | Max. value: 21. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 13066 | short (x10) | RD | Max. value: 23. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 13067 | short (x10) | RD | Max. value: 25. harmonic voltage L3 | V
Maximum values, fourier analysis | 43 | 13068 | short (x1000) | RD | Max. value: 1. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 13069 | short (x1000) | RD | Max. value: 3. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 13070 | short (x1000) | RD | Max. value: 5. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 13071 | short (x1000) | RD | Max. value: 7. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 13072 | short (x1000) | RD | Max. value: 9. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 13073 | short (x1000) | RD | Max. value: 11. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 13074 | short (x1000) | RD | Max. value: 13. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 13075 | short (x1000) | RD | Max. value: 15. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 13076 | short (x1000) | RD | Max. value: 17. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 13077 | short (x1000) | RD | Max. value: 19. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 13078 | short (x1000) | RD | Max. value: 21. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 13079 | short (x1000) | RD | Max. value: 23. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 13080 | short (x1000) | RD | Max. value: 25. harmonic current L1 | A
Maximum values, fourier analysis | 43 | 13081 | short (x1000) | RD | Max. value: 1. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 13082 | short (x1000) | RD | Max. value: 3. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 13083 | short (x1000) | RD | Max. value: 5. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 13084 | short (x1000) | RD | Max. value: 7. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 13085 | short (x1000) | RD | Max. value: 9. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 13086 | short (x1000) | RD | Max. value: 11. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 13087 | short (x1000) | RD | Max. value: 13. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 13088 | short (x1000) | RD | Max. value: 15. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 13089 | short (x1000) | RD | Max. value: 17. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 13090 | short (x1000) | RD | Max. value: 19. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 13091 | short (x1000) | RD | Max. value: 21. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 13092 | short (x1000) | RD | Max. value: 23. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 13093 | short (x1000) | RD | Max. value: 25. harmonic current L2 | A
Maximum values, fourier analysis | 43 | 13094 | short (x1000) | RD | Max. value: 1. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 13095 | short (x1000) | RD | Max. value: 3. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 13096 | short (x1000) | RD | Max. value: 5. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 13097 | short (x1000) | RD | Max. value: 7. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 13098 | short (x1000) | RD | Max. value: 9. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 13099 | short (x1000) | RD | Max. value: 11. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 13100 | short (x1000) | RD | Max. value: 13. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 13101 | short (x1000) | RD | Max. value: 15. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 13102 | short (x1000) | RD | Max. value: 17. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 13103 | short (x1000) | RD | Max. value: 17. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 13104 | short (x1000) | RD | Max. value: 21. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 13105 | short (x1000) | RD | Max. value: 23. harmonic current L3 | A
Maximum values, fourier analysis | 43 | 13106 | short (x1000) | RD | Max. value: 25. harmonic current L3 | A
Maximum values, timestamp, fourier analysis | 45 | 3358 | uint | RD | UTC timestamp, max. value: 1. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 3360 | uint | RD | UTC timestamp, max. value: 3. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 3362 | uint | RD | UTC timestamp, max. value: 5. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 3364 | uint | RD | UTC timestamp, max. value: 7. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 3366 | uint | RD | UTC timestamp, max. value: 9. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 3368 | uint | RD | UTC timestamp, max. value: 11. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 3370 | uint | RD | UTC timestamp, max. value: 13. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 3372 | uint | RD | UTC timestamp, max. value: 15. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 3374 | uint | RD | UTC timestamp, max. value: 17. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 3376 | uint | RD | UTC timestamp, max. value: 19. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 3378 | uint | RD | UTC timestamp, max. value: 21. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 3380 | uint | RD | UTC timestamp, max. value: 23. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 3382 | uint | RD | UTC timestamp, max. value: 25. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 3384 | uint | RD | UTC timestamp, max. value: 1. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 3386 | uint | RD | UTC timestamp, max. value: 3. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 3388 | uint | RD | UTC timestamp, max. value: 5. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 3390 | uint | RD | UTC timestamp, max. value: 7. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 3392 | uint | RD | UTC timestamp, max. value: 9. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 3394 | uint | RD | UTC timestamp, max. value: 11. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 3396 | uint | RD | UTC timestamp, max. value: 13. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 3398 | uint | RD | UTC timestamp, max. value: 15. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 3400 | uint | RD | UTC timestamp, max. value: 17. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 3402 | uint | RD | UTC timestamp, max. value: 19. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 3404 | uint | RD | UTC timestamp, max. value: 21. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 3406 | uint | RD | UTC timestamp, max. value: 23. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 3408 | uint | RD | UTC timestamp, max. value: 25. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 3410 | uint | RD | UTC timestamp, max. value: 1. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 3412 | uint | RD | UTC timestamp, max. value: 3. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 3414 | uint | RD | UTC timestamp, max. value: 5. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 3416 | uint | RD | UTC timestamp, max. value: 7. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 3418 | uint | RD | UTC timestamp, max. value: 9. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 3420 | uint | RD | UTC timestamp, max. value: 11. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 3422 | uint | RD | UTC timestamp, max. value: 13. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 3424 | uint | RD | UTC timestamp, max. value: 15. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 3426 | uint | RD | UTC timestamp, max. value: 17. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 3428 | uint | RD | UTC timestamp, max. value: 19. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 3430 | uint | RD | UTC timestamp, max. value: 21. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 3432 | uint | RD | UTC timestamp, max. value: 23. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 3434 | uint | RD | UTC timestamp, max. value: 25. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 3436 | uint | RD | UTC timestamp, max. value: 1. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 3438 | uint | RD | UTC timestamp, max. value: 3. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 3440 | uint | RD | UTC timestamp, max. value: 5. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 3442 | uint | RD | UTC timestamp, max. value: 7. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 3444 | uint | RD | UTC timestamp, max. value: 9. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 3446 | uint | RD | UTC timestamp, max. value: 11. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 3448 | uint | RD | UTC timestamp, max. value: 13. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 3450 | uint | RD | UTC timestamp, max. value: 15. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 3452 | uint | RD | UTC timestamp, max. value: 17. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 3454 | uint | RD | UTC timestamp, max. value: 19. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 3456 | uint | RD | UTC timestamp, max. value: 21. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 3458 | uint | RD | UTC timestamp, max. value: 23. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 3460 | uint | RD | UTC timestamp, max. value: 25. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 3462 | uint | RD | UTC timestamp, max. value: 1. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 3464 | uint | RD | UTC timestamp, max. value: 3. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 3466 | uint | RD | UTC timestamp, max. value: 5. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 3468 | uint | RD | UTC timestamp, max. value: 7. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 3470 | uint | RD | UTC timestamp, max. value: 9. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 3472 | uint | RD | UTC timestamp, max. value: 11. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 3474 | uint | RD | UTC timestamp, max. value: 13. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 3476 | uint | RD | UTC timestamp, max. value: 15. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 3478 | uint | RD | UTC timestamp, max. value: 17. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 3480 | uint | RD | UTC timestamp, max. value: 19. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 3482 | uint | RD | UTC timestamp, max. value: 21. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 3484 | uint | RD | UTC timestamp, max. value: 23. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 3486 | uint | RD | UTC timestamp, max. value: 25. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 3488 | uint | RD | UTC timestamp, max. value: 1. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 3490 | uint | RD | UTC timestamp, max. value: 3. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 3492 | uint | RD | UTC timestamp, max. value: 5. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 3494 | uint | RD | UTC timestamp, max. value: 7. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 3496 | uint | RD | UTC timestamp, max. value: 9. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 3498 | uint | RD | UTC timestamp, max. value: 11. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 3500 | uint | RD | UTC timestamp, max. value: 13. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 3502 | uint | RD | UTC timestamp, max. value: 15. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 3504 | uint | RD | UTC timestamp, max. value: 17. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 3506 | uint | RD | UTC timestamp, max. value: 19. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 3508 | uint | RD | UTC timestamp, max. value: 21. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 3510 | uint | RD | UTC timestamp, max. value: 23. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 3512 | uint | RD | UTC timestamp, max. value: 25. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9440 | uint | RD | UTC timestamp, max. value: 1. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9442 | uint | RD | UTC timestamp, max. value: 2. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9444 | uint | RD | UTC timestamp, max. value: 3. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9446 | uint | RD | UTC timestamp, max. value: 4. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9448 | uint | RD | UTC timestamp, max. value: 5. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9450 | uint | RD | UTC timestamp, max. value: 6. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9452 | uint | RD | UTC timestamp, max. value: 7. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9454 | uint | RD | UTC timestamp, max. value: 8. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9456 | uint | RD | UTC timestamp, max. value: 9. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9458 | uint | RD | UTC timestamp, max. value: 10. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9460 | uint | RD | UTC timestamp, max. value: 11. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9462 | uint | RD | UTC timestamp, max. value: 12. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9464 | uint | RD | UTC timestamp, max. value: 13. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9466 | uint | RD | UTC timestamp, max. value: 14. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9468 | uint | RD | UTC timestamp, max. value: 15. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9470 | uint | RD | UTC timestamp, max. value: 16. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9472 | uint | RD | UTC timestamp, max. value: 17. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9474 | uint | RD | UTC timestamp, max. value: 18. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9476 | uint | RD | UTC timestamp, max. value: 19. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9478 | uint | RD | UTC timestamp, max. value: 20. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9480 | uint | RD | UTC timestamp, max. value: 21. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9482 | uint | RD | UTC timestamp, max. value: 22. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9484 | uint | RD | UTC timestamp, max. value: 23. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9486 | uint | RD | UTC timestamp, max. value: 24. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9488 | uint | RD | UTC timestamp, max. value: 25. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9490 | uint | RD | UTC timestamp, max. value: 26. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9492 | uint | RD | UTC timestamp, max. value: 27. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9494 | uint | RD | UTC timestamp, max. value: 28. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9496 | uint | RD | UTC timestamp, max. value: 29. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9498 | uint | RD | UTC timestamp, max. value: 30. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9500 | uint | RD | UTC timestamp, max. value: 31. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9502 | uint | RD | UTC timestamp, max. value: 32. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9504 | uint | RD | UTC timestamp, max. value: 33. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9506 | uint | RD | UTC timestamp, max. value: 34. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9508 | uint | RD | UTC timestamp, max. value: 35. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9510 | uint | RD | UTC timestamp, max. value: 36. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9512 | uint | RD | UTC timestamp, max. value: 37. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9514 | uint | RD | UTC timestamp, max. value: 38. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9516 | uint | RD | UTC timestamp, max. value: 39. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9518 | uint | RD | UTC timestamp, max. value: 40. harmonic voltage L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9520 | uint | RD | UTC timestamp, max. value: 1. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9522 | uint | RD | UTC timestamp, max. value: 2. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9524 | uint | RD | UTC timestamp, max. value: 3. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9526 | uint | RD | UTC timestamp, max. value: 4. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9528 | uint | RD | UTC timestamp, max. value: 5. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9530 | uint | RD | UTC timestamp, max. value: 6. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9532 | uint | RD | UTC timestamp, max. value: 7. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9534 | uint | RD | UTC timestamp, max. value: 8. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9536 | uint | RD | UTC timestamp, max. value: 9. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9538 | uint | RD | UTC timestamp, max. value: 10. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9540 | uint | RD | UTC timestamp, max. value: 11. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9542 | uint | RD | UTC timestamp, max. value: 12. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9544 | uint | RD | UTC timestamp, max. value: 13. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9546 | uint | RD | UTC timestamp, max. value: 14. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9548 | uint | RD | UTC timestamp, max. value: 15. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9550 | uint | RD | UTC timestamp, max. value: 16. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9552 | uint | RD | UTC timestamp, max. value: 17. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9554 | uint | RD | UTC timestamp, max. value: 18. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9556 | uint | RD | UTC timestamp, max. value: 19. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9558 | uint | RD | UTC timestamp, max. value: 20. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9560 | uint | RD | UTC timestamp, max. value: 21. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9562 | uint | RD | UTC timestamp, max. value: 22. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9564 | uint | RD | UTC timestamp, max. value: 23. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9566 | uint | RD | UTC timestamp, max. value: 24. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9568 | uint | RD | UTC timestamp, max. value: 25. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9570 | uint | RD | UTC timestamp, max. value: 26. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9572 | uint | RD | UTC timestamp, max. value: 27. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9574 | uint | RD | UTC timestamp, max. value: 28. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9576 | uint | RD | UTC timestamp, max. value: 29. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9578 | uint | RD | UTC timestamp, max. value: 30. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9580 | uint | RD | UTC timestamp, max. value: 31. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9582 | uint | RD | UTC timestamp, max. value: 32. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9584 | uint | RD | UTC timestamp, max. value: 33. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9586 | uint | RD | UTC timestamp, max. value: 34. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9588 | uint | RD | UTC timestamp, max. value: 35. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9590 | uint | RD | UTC timestamp, max. value: 36. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9592 | uint | RD | UTC timestamp, max. value: 37. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9594 | uint | RD | UTC timestamp, max. value: 38. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9596 | uint | RD | UTC timestamp, max. value: 39. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9598 | uint | RD | UTC timestamp, max. value: 40. harmonic voltage L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9600 | uint | RD | UTC timestamp, max. value: 1. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9602 | uint | RD | UTC timestamp, max. value: 2. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9604 | uint | RD | UTC timestamp, max. value: 3. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9606 | uint | RD | UTC timestamp, max. value: 4. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9608 | uint | RD | UTC timestamp, max. value: 5. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9610 | uint | RD | UTC timestamp, max. value: 6. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9612 | uint | RD | UTC timestamp, max. value: 7. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9614 | uint | RD | UTC timestamp, max. value: 8. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9616 | uint | RD | UTC timestamp, max. value: 9. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9618 | uint | RD | UTC timestamp, max. value: 10. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9620 | uint | RD | UTC timestamp, max. value: 11. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9622 | uint | RD | UTC timestamp, max. value: 12. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9624 | uint | RD | UTC timestamp, max. value: 13. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9626 | uint | RD | UTC timestamp, max. value: 14. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9628 | uint | RD | UTC timestamp, max. value: 15. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9630 | uint | RD | UTC timestamp, max. value: 16. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9632 | uint | RD | UTC timestamp, max. value: 17. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9634 | uint | RD | UTC timestamp, max. value: 18. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9636 | uint | RD | UTC timestamp, max. value: 19. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9638 | uint | RD | UTC timestamp, max. value: 20. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9640 | uint | RD | UTC timestamp, max. value: 21. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9642 | uint | RD | UTC timestamp, max. value: 22. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9644 | uint | RD | UTC timestamp, max. value: 23. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9646 | uint | RD | UTC timestamp, max. value: 24. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9648 | uint | RD | UTC timestamp, max. value: 25. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9650 | uint | RD | UTC timestamp, max. value: 26. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9652 | uint | RD | UTC timestamp, max. value: 27. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9654 | uint | RD | UTC timestamp, max. value: 28. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9656 | uint | RD | UTC timestamp, max. value: 29. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9658 | uint | RD | UTC timestamp, max. value: 30. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9660 | uint | RD | UTC timestamp, max. value: 31. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9662 | uint | RD | UTC timestamp, max. value: 32. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9664 | uint | RD | UTC timestamp, max. value: 33. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9666 | uint | RD | UTC timestamp, max. value: 34. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9668 | uint | RD | UTC timestamp, max. value: 35. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9670 | uint | RD | UTC timestamp, max. value: 36. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9672 | uint | RD | UTC timestamp, max. value: 37. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9674 | uint | RD | UTC timestamp, max. value: 38. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9676 | uint | RD | UTC timestamp, max. value: 39. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9678 | uint | RD | UTC timestamp, max. value: 40. harmonic voltage L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9680 | uint | RD | UTC timestamp, max. value: 1. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9682 | uint | RD | UTC timestamp, max. value: 2. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9684 | uint | RD | UTC timestamp, max. value: 3. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9686 | uint | RD | UTC timestamp, max. value: 4. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9688 | uint | RD | UTC timestamp, max. value: 5. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9690 | uint | RD | UTC timestamp, max. value: 6. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9692 | uint | RD | UTC timestamp, max. value: 7. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9694 | uint | RD | UTC timestamp, max. value: 8. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9696 | uint | RD | UTC timestamp, max. value: 9. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9698 | uint | RD | UTC timestamp, max. value: 10. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9700 | uint | RD | UTC timestamp, max. value: 11. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9702 | uint | RD | UTC timestamp, max. value: 12. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9704 | uint | RD | UTC timestamp, max. value: 13. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9706 | uint | RD | UTC timestamp, max. value: 14. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9708 | uint | RD | UTC timestamp, max. value: 15. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9710 | uint | RD | UTC timestamp, max. value: 16. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9712 | uint | RD | UTC timestamp, max. value: 17. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9714 | uint | RD | UTC timestamp, max. value: 18. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9716 | uint | RD | UTC timestamp, max. value: 19. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9718 | uint | RD | UTC timestamp, max. value: 20. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9720 | uint | RD | UTC timestamp, max. value: 21. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9722 | uint | RD | UTC timestamp, max. value: 22. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9724 | uint | RD | UTC timestamp, max. value: 23. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9726 | uint | RD | UTC timestamp, max. value: 24. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9728 | uint | RD | UTC timestamp, max. value: 25. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9730 | uint | RD | UTC timestamp, max. value: 26. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9732 | uint | RD | UTC timestamp, max. value: 27. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9734 | uint | RD | UTC timestamp, max. value: 28. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9736 | uint | RD | UTC timestamp, max. value: 29. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9738 | uint | RD | UTC timestamp, max. value: 30. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9740 | uint | RD | UTC timestamp, max. value: 31. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9742 | uint | RD | UTC timestamp, max. value: 32. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9744 | uint | RD | UTC timestamp, max. value: 33. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9746 | uint | RD | UTC timestamp, max. value: 34. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9748 | uint | RD | UTC timestamp, max. value: 35. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9750 | uint | RD | UTC timestamp, max. value: 36. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9752 | uint | RD | UTC timestamp, max. value: 37. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9754 | uint | RD | UTC timestamp, max. value: 38. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9756 | uint | RD | UTC timestamp, max. value: 39. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9758 | uint | RD | UTC timestamp, max. value: 40. harmonic current L1 | s
Maximum values, timestamp, fourier analysis | 45 | 9760 | uint | RD | UTC timestamp, max. value: 1. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9762 | uint | RD | UTC timestamp, max. value: 2. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9764 | uint | RD | UTC timestamp, max. value: 3. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9766 | uint | RD | UTC timestamp, max. value: 4. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9768 | uint | RD | UTC timestamp, max. value: 5. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9770 | uint | RD | UTC timestamp, max. value: 6. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9772 | uint | RD | UTC timestamp, max. value: 7. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9774 | uint | RD | UTC timestamp, max. value: 8. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9776 | uint | RD | UTC timestamp, max. value: 9. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9778 | uint | RD | UTC timestamp, max. value: 10. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9780 | uint | RD | UTC timestamp, max. value: 11. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9782 | uint | RD | UTC timestamp, max. value: 12. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9784 | uint | RD | UTC timestamp, max. value: 13. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9786 | uint | RD | UTC timestamp, max. value: 14. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9788 | uint | RD | UTC timestamp, max. value: 15. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9790 | uint | RD | UTC timestamp, max. value: 16. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9792 | uint | RD | UTC timestamp, max. value: 17. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9794 | uint | RD | UTC timestamp, max. value: 18. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9796 | uint | RD | UTC timestamp, max. value: 19. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9798 | uint | RD | UTC timestamp, max. value: 20. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9800 | uint | RD | UTC timestamp, max. value: 21. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9802 | uint | RD | UTC timestamp, max. value: 22. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9804 | uint | RD | UTC timestamp, max. value: 23. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9806 | uint | RD | UTC timestamp, max. value: 24. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9808 | uint | RD | UTC timestamp, max. value: 25. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9810 | uint | RD | UTC timestamp, max. value: 26. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9812 | uint | RD | UTC timestamp, max. value: 27. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9814 | uint | RD | UTC timestamp, max. value: 28. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9816 | uint | RD | UTC timestamp, max. value: 29. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9818 | uint | RD | UTC timestamp, max. value: 30. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9820 | uint | RD | UTC timestamp, max. value: 31. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9822 | uint | RD | UTC timestamp, max. value: 32. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9824 | uint | RD | UTC timestamp, max. value: 33. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9826 | uint | RD | UTC timestamp, max. value: 34. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9828 | uint | RD | UTC timestamp, max. value: 35. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9830 | uint | RD | UTC timestamp, max. value: 36. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9832 | uint | RD | UTC timestamp, max. value: 37. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9834 | uint | RD | UTC timestamp, max. value: 38. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9836 | uint | RD | UTC timestamp, max. value: 39. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9838 | uint | RD | UTC timestamp, max. value: 40. harmonic current L2 | s
Maximum values, timestamp, fourier analysis | 45 | 9840 | uint | RD | UTC timestamp, max. value: 1. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9842 | uint | RD | UTC timestamp, max. value: 2. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9844 | uint | RD | UTC timestamp, max. value: 3. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9846 | uint | RD | UTC timestamp, max. value: 4. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9848 | uint | RD | UTC timestamp, max. value: 5. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9850 | uint | RD | UTC timestamp, max. value: 6. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9852 | uint | RD | UTC timestamp, max. value: 7. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9854 | uint | RD | UTC timestamp, max. value: 8. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9856 | uint | RD | UTC timestamp, max. value: 9. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9858 | uint | RD | UTC timestamp, max. value: 10. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9860 | uint | RD | UTC timestamp, max. value: 11. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9862 | uint | RD | UTC timestamp, max. value: 12. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9864 | uint | RD | UTC timestamp, max. value: 13. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9866 | uint | RD | UTC timestamp, max. value: 14. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9868 | uint | RD | UTC timestamp, max. value: 15. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9870 | uint | RD | UTC timestamp, max. value: 16. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9872 | uint | RD | UTC timestamp, max. value: 17. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9874 | uint | RD | UTC timestamp, max. value: 18. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9876 | uint | RD | UTC timestamp, max. value: 19. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9878 | uint | RD | UTC timestamp, max. value: 20. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9880 | uint | RD | UTC timestamp, max. value: 21. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9882 | uint | RD | UTC timestamp, max. value: 22. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9884 | uint | RD | UTC timestamp, max. value: 23. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9886 | uint | RD | UTC timestamp, max. value: 24. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9888 | uint | RD | UTC timestamp, max. value: 25. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9890 | uint | RD | UTC timestamp, max. value: 26. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9892 | uint | RD | UTC timestamp, max. value: 27. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9894 | uint | RD | UTC timestamp, max. value: 28. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9896 | uint | RD | UTC timestamp, max. value: 29. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9898 | uint | RD | UTC timestamp, max. value: 30. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9900 | uint | RD | UTC timestamp, max. value: 31. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9902 | uint | RD | UTC timestamp, max. value: 32. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9904 | uint | RD | UTC timestamp, max. value: 33. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9906 | uint | RD | UTC timestamp, max. value: 34. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9908 | uint | RD | UTC timestamp, max. value: 35. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9910 | uint | RD | UTC timestamp, max. value: 36. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9912 | uint | RD | UTC timestamp, max. value: 37. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9914 | uint | RD | UTC timestamp, max. value: 38. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9916 | uint | RD | UTC timestamp, max. value: 39. harmonic current L3 | s
Maximum values, timestamp, fourier analysis | 45 | 9918 | uint | RD | UTC timestamp, max. value: 40. harmonic current L3 | s
Minimum values, fourier analysis | 46 | 4020 | float | RD | Min. value: 1. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 4022 | float | RD | Min. value: 3. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 4024 | float | RD | Min. value: 5. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 4026 | float | RD | Min. value: 7. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 4028 | float | RD | Min. value: 9. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 4030 | float | RD | Min. value: 11. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 4032 | float | RD | Min. value: 13. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 4034 | float | RD | Min. value: 15. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 4036 | float | RD | Min. value: 17. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 4038 | float | RD | Min. value: 19. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 4040 | float | RD | Min. value: 21. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 4042 | float | RD | Min. value: 23. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 4044 | float | RD | Min. value: 25. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 4046 | float | RD | Min. value: 1. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 4048 | float | RD | Min. value: 3. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 4050 | float | RD | Min. value: 5. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 4052 | float | RD | Min. value: 7. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 4054 | float | RD | Min. value: 9. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 4056 | float | RD | Min. value: 11. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 4058 | float | RD | Min. value: 13. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 4060 | float | RD | Min. value: 15. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 4062 | float | RD | Min. value: 17. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 4064 | float | RD | Min. value: 19. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 4066 | float | RD | Min. value: 21. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 4068 | float | RD | Min. value: 23. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 4070 | float | RD | Min. value: 25. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 4072 | float | RD | Min. value: 1. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 4074 | float | RD | Min. value: 3. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 4076 | float | RD | Min. value: 5. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 4078 | float | RD | Min. value: 7. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 4080 | float | RD | Min. value: 9. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 4082 | float | RD | Min. value: 11. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 4084 | float | RD | Min. value: 13. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 4086 | float | RD | Min. value: 15. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 4088 | float | RD | Min. value: 17. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 4090 | float | RD | Min. value: 19. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 4092 | float | RD | Min. value: 21. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 4094 | float | RD | Min. value: 23. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 4096 | float | RD | Min. value: 25. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 9920 | float | RD | Min. value: 1. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9922 | float | RD | Min. value: 2. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9924 | float | RD | Min. value: 3. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9926 | float | RD | Min. value: 4. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9928 | float | RD | Min. value: 5. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9930 | float | RD | Min. value: 6. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9932 | float | RD | Min. value: 7. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9934 | float | RD | Min. value: 8. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9936 | float | RD | Min. value: 9. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9938 | float | RD | Min. value: 10. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9940 | float | RD | Min. value: 11. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9942 | float | RD | Min. value: 12. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9944 | float | RD | Min. value: 13. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9946 | float | RD | Min. value: 14. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9948 | float | RD | Min. value: 15. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9950 | float | RD | Min. value: 16. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9952 | float | RD | Min. value: 17. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9954 | float | RD | Min. value: 18. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9956 | float | RD | Min. value: 19. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9958 | float | RD | Min. value: 20. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9960 | float | RD | Min. value: 21. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9962 | float | RD | Min. value: 22. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9964 | float | RD | Min. value: 23. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9966 | float | RD | Min. value: 24. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9968 | float | RD | Min. value: 25. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9970 | float | RD | Min. value: 26. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9972 | float | RD | Min. value: 27. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9974 | float | RD | Min. value: 28. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9976 | float | RD | Min. value: 29. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9978 | float | RD | Min. value: 30. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9980 | float | RD | Min. value: 31. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9982 | float | RD | Min. value: 32. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9984 | float | RD | Min. value: 33. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9986 | float | RD | Min. value: 34. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9988 | float | RD | Min. value: 35. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9990 | float | RD | Min. value: 36. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9992 | float | RD | Min. value: 37. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9994 | float | RD | Min. value: 38. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9996 | float | RD | Min. value: 39. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 9998 | float | RD | Min. value: 40. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 10000 | float | RD | Min. value: 1. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10002 | float | RD | Min. value: 2. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10004 | float | RD | Min. value: 3. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10006 | float | RD | Min. value: 4. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10008 | float | RD | Min. value: 5. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10010 | float | RD | Min. value: 6. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10012 | float | RD | Min. value: 7. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10014 | float | RD | Min. value: 8. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10016 | float | RD | Min. value: 9. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10018 | float | RD | Min. value: 10. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10020 | float | RD | Min. value: 11. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10022 | float | RD | Min. value: 12. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10024 | float | RD | Min. value: 13. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10026 | float | RD | Min. value: 14. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10028 | float | RD | Min. value: 15. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10030 | float | RD | Min. value: 16. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10032 | float | RD | Min. value: 17. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10034 | float | RD | Min. value: 18. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10036 | float | RD | Min. value: 19. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10038 | float | RD | Min. value: 20. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10040 | float | RD | Min. value: 21. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10042 | float | RD | Min. value: 22. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10044 | float | RD | Min. value: 23. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10046 | float | RD | Min. value: 24. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10048 | float | RD | Min. value: 25. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10050 | float | RD | Min. value: 26. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10052 | float | RD | Min. value: 27. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10054 | float | RD | Min. value: 28. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10056 | float | RD | Min. value: 29. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10058 | float | RD | Min. value: 30. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10060 | float | RD | Min. value: 31. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10062 | float | RD | Min. value: 32. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10064 | float | RD | Min. value: 33. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10066 | float | RD | Min. value: 34. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10068 | float | RD | Min. value: 35. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10070 | float | RD | Min. value: 36. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10072 | float | RD | Min. value: 37. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10074 | float | RD | Min. value: 38. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10076 | float | RD | Min. value: 39. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10078 | float | RD | Min. value: 40. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 10080 | float | RD | Min. value: 1. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10082 | float | RD | Min. value: 2. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10084 | float | RD | Min. value: 3. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10086 | float | RD | Min. value: 4. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10088 | float | RD | Min. value: 5. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10090 | float | RD | Min. value: 6. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10092 | float | RD | Min. value: 7. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10094 | float | RD | Min. value: 8. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10096 | float | RD | Min. value: 9. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10098 | float | RD | Min. value: 10. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10100 | float | RD | Min. value: 11. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10102 | float | RD | Min. value: 12. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10104 | float | RD | Min. value: 13. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10106 | float | RD | Min. value: 14. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10108 | float | RD | Min. value: 15. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10110 | float | RD | Min. value: 16. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10112 | float | RD | Min. value: 17. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10114 | float | RD | Min. value: 18. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10116 | float | RD | Min. value: 19. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10118 | float | RD | Min. value: 20. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10120 | float | RD | Min. value: 21. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10122 | float | RD | Min. value: 22. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10124 | float | RD | Min. value: 23. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10126 | float | RD | Min. value: 24. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10128 | float | RD | Min. value: 25. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10130 | float | RD | Min. value: 26. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10132 | float | RD | Min. value: 27. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10134 | float | RD | Min. value: 28. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10136 | float | RD | Min. value: 29. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10138 | float | RD | Min. value: 30. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10140 | float | RD | Min. value: 31. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10142 | float | RD | Min. value: 32. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10144 | float | RD | Min. value: 33. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10146 | float | RD | Min. value: 34. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10148 | float | RD | Min. value: 35. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10150 | float | RD | Min. value: 36. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10152 | float | RD | Min. value: 37. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10154 | float | RD | Min. value: 38. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10156 | float | RD | Min. value: 39. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 10158 | float | RD | Min. value: 40. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 14010 | short (x10) | RD | Min. value: 1. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 14011 | short (x10) | RD | Min. value: 3. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 14012 | short (x10) | RD | Min. value: 5. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 14013 | short (x10) | RD | Min. value: 7. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 14014 | short (x10) | RD | Min. value: 9. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 14015 | short (x10) | RD | Min. value: 11. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 14016 | short (x10) | RD | Min. value: 13. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 14017 | short (x10) | RD | Min. value: 15. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 14018 | short (x10) | RD | Min. value: 17. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 14019 | short (x10) | RD | Min. value: 19. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 14020 | short (x10) | RD | Min. value: 21. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 14021 | short (x10) | RD | Min. value: 23. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 14022 | short (x10) | RD | Min. value: 25. harmonic voltage L1 | V
Minimum values, fourier analysis | 46 | 14023 | short (x10) | RD | Min. value: 1. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 14024 | short (x10) | RD | Min. value: 3. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 14025 | short (x10) | RD | Min. value: 5. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 14026 | short (x10) | RD | Min. value: 7. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 14027 | short (x10) | RD | Min. value: 9. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 14028 | short (x10) | RD | Min. value: 11. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 14029 | short (x10) | RD | Min. value: 13. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 14030 | short (x10) | RD | Min. value: 15. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 14031 | short (x10) | RD | Min. value: 17. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 14032 | short (x10) | RD | Min. value: 19. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 14033 | short (x10) | RD | Min. value: 21. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 14034 | short (x10) | RD | Min. value: 23. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 14035 | short (x10) | RD | Min. value: 25. harmonic voltage L2 | V
Minimum values, fourier analysis | 46 | 14036 | short (x10) | RD | Min. value: 1. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 14037 | short (x10) | RD | Min. value: 3. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 14038 | short (x10) | RD | Min. value: 5. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 14039 | short (x10) | RD | Min. value: 7. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 14040 | short (x10) | RD | Min. value: 9. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 14041 | short (x10) | RD | Min. value: 11. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 14042 | short (x10) | RD | Min. value: 13. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 14043 | short (x10) | RD | Min. value: 15. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 14044 | short (x10) | RD | Min. value: 17. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 14045 | short (x10) | RD | Min. value: 19. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 14046 | short (x10) | RD | Min. value: 21. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 14047 | short (x10) | RD | Min. value: 23. harmonic voltage L3 | V
Minimum values, fourier analysis | 46 | 14048 | short (x10) | RD | Min. value: 25. harmonic voltage L3 | V
Minimum values, timestamp, fourier analysis | 48 | 4220 | uint | RD | UTC timestamp, min. value: 1. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 4222 | uint | RD | UTC timestamp, min. value: 3. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 4224 | uint | RD | UTC timestamp, min. value: 5. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 4226 | uint | RD | UTC timestamp, min. value: 7. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 4228 | uint | RD | UTC timestamp, min. value: 9. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 4230 | uint | RD | UTC timestamp, min. value: 11. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 4232 | uint | RD | UTC timestamp, min. value: 13. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 4234 | uint | RD | UTC timestamp, min. value: 15. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 4236 | uint | RD | UTC timestamp, min. value: 17. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 4238 | uint | RD | UTC timestamp, min. value: 19. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 4240 | uint | RD | UTC timestamp, min. value: 21. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 4242 | uint | RD | UTC timestamp, min. value: 23. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 4244 | uint | RD | UTC timestamp, min. value: 25. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 4246 | uint | RD | UTC timestamp, min. value: 1. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 4248 | uint | RD | UTC timestamp, min. value: 3. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 4250 | uint | RD | UTC timestamp, min. value: 5. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 4252 | uint | RD | UTC timestamp, min. value: 7. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 4254 | uint | RD | UTC timestamp, min. value: 9. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 4256 | uint | RD | UTC timestamp, min. value: 11. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 4258 | uint | RD | UTC timestamp, min. value: 13. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 4260 | uint | RD | UTC timestamp, min. value: 15. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 4262 | uint | RD | UTC timestamp, min. value: 17. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 4264 | uint | RD | UTC timestamp, min. value: 19. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 4266 | uint | RD | UTC timestamp, min. value: 21. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 4268 | uint | RD | UTC timestamp, min. value: 23. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 4270 | uint | RD | UTC timestamp, min. value: 25. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 4272 | uint | RD | UTC timestamp, min. value: 1. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 4274 | uint | RD | UTC timestamp, min. value: 3. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 4276 | uint | RD | UTC timestamp, min. value: 5. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 4278 | uint | RD | UTC timestamp, min. value: 7. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 4280 | uint | RD | UTC timestamp, min. value: 9. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 4282 | uint | RD | UTC timestamp, min. value: 11. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 4284 | uint | RD | UTC timestamp, min. value: 13. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 4286 | uint | RD | UTC timestamp, min. value: 15. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 4288 | uint | RD | UTC timestamp, min. value: 17. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 4290 | uint | RD | UTC timestamp, min. value: 19. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 4292 | uint | RD | UTC timestamp, min. value: 21. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 4294 | uint | RD | UTC timestamp, min. value: 23. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 4296 | uint | RD | UTC timestamp, min. value: 25. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10160 | uint | RD | UTC timestamp, min. value: 1. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10162 | uint | RD | UTC timestamp, min. value: 2. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10164 | uint | RD | UTC timestamp, min. value: 3. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10166 | uint | RD | UTC timestamp, min. value: 4. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10168 | uint | RD | UTC timestamp, min. value: 5. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10170 | uint | RD | UTC timestamp, min. value: 6. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10172 | uint | RD | UTC timestamp, min. value: 7. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10174 | uint | RD | UTC timestamp, min. value: 8. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10176 | uint | RD | UTC timestamp, min. value: 9. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10178 | uint | RD | UTC timestamp, min. value: 10. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10180 | uint | RD | UTC timestamp, min. value: 11. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10182 | uint | RD | UTC timestamp, min. value: 12. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10184 | uint | RD | UTC timestamp, min. value: 13. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10186 | uint | RD | UTC timestamp, min. value: 14. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10188 | uint | RD | UTC timestamp, min. value: 15. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10190 | uint | RD | UTC timestamp, min. value: 16. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10192 | uint | RD | UTC timestamp, min. value: 17. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10194 | uint | RD | UTC timestamp, min. value: 18. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10196 | uint | RD | UTC timestamp, min. value: 19. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10198 | uint | RD | UTC timestamp, min. value: 20. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10200 | uint | RD | UTC timestamp, min. value: 21. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10202 | uint | RD | UTC timestamp, min. value: 22. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10204 | uint | RD | UTC timestamp, min. value: 23. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10206 | uint | RD | UTC timestamp, min. value: 24. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10208 | uint | RD | UTC timestamp, min. value: 25. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10210 | uint | RD | UTC timestamp, min. value: 26. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10212 | uint | RD | UTC timestamp, min. value: 27. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10214 | uint | RD | UTC timestamp, min. value: 28. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10216 | uint | RD | UTC timestamp, min. value: 29. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10218 | uint | RD | UTC timestamp, min. value: 30. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10220 | uint | RD | UTC timestamp, min. value: 31. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10222 | uint | RD | UTC timestamp, min. value: 32. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10224 | uint | RD | UTC timestamp, min. value: 33. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10226 | uint | RD | UTC timestamp, min. value: 34. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10228 | uint | RD | UTC timestamp, min. value: 35. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10230 | uint | RD | UTC timestamp, min. value: 36. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10232 | uint | RD | UTC timestamp, min. value: 37. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10234 | uint | RD | UTC timestamp, min. value: 38. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10236 | uint | RD | UTC timestamp, min. value: 39. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10238 | uint | RD | UTC timestamp, min. value: 40. harmonic voltage L1 | s
Minimum values, timestamp, fourier analysis | 48 | 10240 | uint | RD | UTC timestamp, min. value: 1. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10242 | uint | RD | UTC timestamp, min. value: 2. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10244 | uint | RD | UTC timestamp, min. value: 3. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10246 | uint | RD | UTC timestamp, min. value: 4. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10248 | uint | RD | UTC timestamp, min. value: 5. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10250 | uint | RD | UTC timestamp, min. value: 6. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10252 | uint | RD | UTC timestamp, min. value: 7. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10254 | uint | RD | UTC timestamp, min. value: 8. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10256 | uint | RD | UTC timestamp, min. value: 9. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10258 | uint | RD | UTC timestamp, min. value: 10. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10260 | uint | RD | UTC timestamp, min. value: 11. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10262 | uint | RD | UTC timestamp, min. value: 12. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10264 | uint | RD | UTC timestamp, min. value: 13. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10266 | uint | RD | UTC timestamp, min. value: 14. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10268 | uint | RD | UTC timestamp, min. value: 15. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10270 | uint | RD | UTC timestamp, min. value: 16. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10272 | uint | RD | UTC timestamp, min. value: 17. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10274 | uint | RD | UTC timestamp, min. value: 18. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10276 | uint | RD | UTC timestamp, min. value: 19. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10278 | uint | RD | UTC timestamp, min. value: 20. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10280 | uint | RD | UTC timestamp, min. value: 21. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10282 | uint | RD | UTC timestamp, min. value: 22. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10284 | uint | RD | UTC timestamp, min. value: 23. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10286 | uint | RD | UTC timestamp, min. value: 24. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10288 | uint | RD | UTC timestamp, min. value: 25. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10290 | uint | RD | UTC timestamp, min. value: 26. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10292 | uint | RD | UTC timestamp, min. value: 27. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10294 | uint | RD | UTC timestamp, min. value: 28. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10296 | uint | RD | UTC timestamp, min. value: 29. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10298 | uint | RD | UTC timestamp, min. value: 30. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10300 | uint | RD | UTC timestamp, min. value: 31. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10302 | uint | RD | UTC timestamp, min. value: 32. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10304 | uint | RD | UTC timestamp, min. value: 33. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10306 | uint | RD | UTC timestamp, min. value: 34. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10308 | uint | RD | UTC timestamp, min. value: 35. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10310 | uint | RD | UTC timestamp, min. value: 36. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10312 | uint | RD | UTC timestamp, min. value: 37. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10314 | uint | RD | UTC timestamp, min. value: 38. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10316 | uint | RD | UTC timestamp, min. value: 39. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10318 | uint | RD | UTC timestamp, min. value: 40. harmonic voltage L2 | s
Minimum values, timestamp, fourier analysis | 48 | 10320 | uint | RD | UTC timestamp, min. value: 1. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10322 | uint | RD | UTC timestamp, min. value: 2. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10324 | uint | RD | UTC timestamp, min. value: 3. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10326 | uint | RD | UTC timestamp, min. value: 4. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10328 | uint | RD | UTC timestamp, min. value: 5. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10330 | uint | RD | UTC timestamp, min. value: 6. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10332 | uint | RD | UTC timestamp, min. value: 7. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10334 | uint | RD | UTC timestamp, min. value: 8. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10336 | uint | RD | UTC timestamp, min. value: 9. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10338 | uint | RD | UTC timestamp, min. value: 10. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10340 | uint | RD | UTC timestamp, min. value: 11. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10342 | uint | RD | UTC timestamp, min. value: 12. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10344 | uint | RD | UTC timestamp, min. value: 13. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10346 | uint | RD | UTC timestamp, min. value: 14. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10348 | uint | RD | UTC timestamp, min. value: 15. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10350 | uint | RD | UTC timestamp, min. value: 16. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10352 | uint | RD | UTC timestamp, min. value: 17. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10354 | uint | RD | UTC timestamp, min. value: 18. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10356 | uint | RD | UTC timestamp, min. value: 19. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10358 | uint | RD | UTC timestamp, min. value: 20. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10360 | uint | RD | UTC timestamp, min. value: 21. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10362 | uint | RD | UTC timestamp, min. value: 22. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10364 | uint | RD | UTC timestamp, min. value: 23. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10366 | uint | RD | UTC timestamp, min. value: 24. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10368 | uint | RD | UTC timestamp, min. value: 25. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10370 | uint | RD | UTC timestamp, min. value: 26. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10372 | uint | RD | UTC timestamp, min. value: 27. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10374 | uint | RD | UTC timestamp, min. value: 28. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10376 | uint | RD | UTC timestamp, min. value: 29. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10378 | uint | RD | UTC timestamp, min. value: 30. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10380 | uint | RD | UTC timestamp, min. value: 31. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10382 | uint | RD | UTC timestamp, min. value: 32. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10384 | uint | RD | UTC timestamp, min. value: 33. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10386 | uint | RD | UTC timestamp, min. value: 34. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10388 | uint | RD | UTC timestamp, min. value: 35. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10390 | uint | RD | UTC timestamp, min. value: 36. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10392 | uint | RD | UTC timestamp, min. value: 37. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10394 | uint | RD | UTC timestamp, min. value: 38. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10396 | uint | RD | UTC timestamp, min. value: 39. harmonic voltage L3 | s
Minimum values, timestamp, fourier analysis | 48 | 10398 | uint | RD | UTC timestamp, min. value: 40. harmonic voltage L3 | s
Moving mean values, fourier analysis | 49 | 2058 | float | RD | Mean value: 1. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 2060 | float | RD | Mean value: 3. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 2062 | float | RD | Mean value: 5. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 2064 | float | RD | Mean value: 7. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 2066 | float | RD | Mean value: 9. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 2068 | float | RD | Mean value: 11. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 2070 | float | RD | Mean value: 13. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 2072 | float | RD | Mean value: 15. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 2074 | float | RD | Mean value: 17. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 2076 | float | RD | Mean value: 19. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 2078 | float | RD | Mean value: 21. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 2080 | float | RD | Mean value: 23. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 2082 | float | RD | Mean value: 25. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 2084 | float | RD | Mean value: 1. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 2086 | float | RD | Mean value: 3. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 2088 | float | RD | Mean value: 5. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 2090 | float | RD | Mean value: 7. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 2092 | float | RD | Mean value: 9. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 2094 | float | RD | Mean value: 11. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 2096 | float | RD | Mean value: 13. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 2098 | float | RD | Mean value: 15. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 2100 | float | RD | Mean value: 17. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 2102 | float | RD | Mean value: 19. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 2104 | float | RD | Mean value: 21. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 2106 | float | RD | Mean value: 23. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 2108 | float | RD | Mean value: 25. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 2110 | float | RD | Mean value: 1. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 2112 | float | RD | Mean value: 3. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 2114 | float | RD | Mean value: 5. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 2116 | float | RD | Mean value: 7. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 2118 | float | RD | Mean value: 9. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 2120 | float | RD | Mean value: 11. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 2122 | float | RD | Mean value: 13. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 2124 | float | RD | Mean value: 15. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 2126 | float | RD | Mean value: 17. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 2128 | float | RD | Mean value: 19. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 2130 | float | RD | Mean value: 21. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 2132 | float | RD | Mean value: 23. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 2134 | float | RD | Mean value: 25. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 2136 | float | RD | Mean value: 1. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 2138 | float | RD | Mean value: 3. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 2140 | float | RD | Mean value: 5. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 2142 | float | RD | Mean value: 7. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 2144 | float | RD | Mean value: 9. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 2146 | float | RD | Mean value: 11. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 2148 | float | RD | Mean value: 13. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 2150 | float | RD | Mean value: 15. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 2152 | float | RD | Mean value: 17. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 2154 | float | RD | Mean value: 19. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 2156 | float | RD | Mean value: 21. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 2158 | float | RD | Mean value: 23. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 2160 | float | RD | Mean value: 25. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 2162 | float | RD | Mean value: 1. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 2164 | float | RD | Mean value: 3. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 2166 | float | RD | Mean value: 5. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 2168 | float | RD | Mean value: 7. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 2170 | float | RD | Mean value: 9. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 2172 | float | RD | Mean value: 11. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 2174 | float | RD | Mean value: 13. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 2176 | float | RD | Mean value: 15. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 2178 | float | RD | Mean value: 17. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 2180 | float | RD | Mean value: 19. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 2182 | float | RD | Mean value: 21. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 2184 | float | RD | Mean value: 23. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 2186 | float | RD | Mean value: 25. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 2188 | float | RD | Mean value: 1. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 2190 | float | RD | Mean value: 3. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 2192 | float | RD | Mean value: 5. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 2194 | float | RD | Mean value: 7. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 2196 | float | RD | Mean value: 9. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 2198 | float | RD | Mean value: 11. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 2200 | float | RD | Mean value: 13. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 2202 | float | RD | Mean value: 15. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 2204 | float | RD | Mean value: 17. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 2206 | float | RD | Mean value: 19. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 2208 | float | RD | Mean value: 21. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 2210 | float | RD | Mean value: 23. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 2212 | float | RD | Mean value: 25. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8480 | float | RD | Mean value: 1. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8482 | float | RD | Mean value: 2. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8484 | float | RD | Mean value: 3. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8486 | float | RD | Mean value: 4. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8488 | float | RD | Mean value: 5. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8490 | float | RD | Mean value: 6. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8492 | float | RD | Mean value: 7. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8494 | float | RD | Mean value: 8. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8496 | float | RD | Mean value: 9. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8498 | float | RD | Mean value: 10. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8500 | float | RD | Mean value: 11. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8502 | float | RD | Mean value: 12. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8504 | float | RD | Mean value: 13. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8506 | float | RD | Mean value: 14. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8508 | float | RD | Mean value: 15. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8510 | float | RD | Mean value: 16. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8512 | float | RD | Mean value: 17. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8514 | float | RD | Mean value: 18. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8516 | float | RD | Mean value: 19. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8518 | float | RD | Mean value: 20. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8520 | float | RD | Mean value: 21. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8522 | float | RD | Mean value: 22. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8524 | float | RD | Mean value: 23. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8526 | float | RD | Mean value: 24. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8528 | float | RD | Mean value: 25. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8530 | float | RD | Mean value: 26. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8532 | float | RD | Mean value: 27. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8534 | float | RD | Mean value: 28. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8536 | float | RD | Mean value: 29. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8538 | float | RD | Mean value: 30. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8540 | float | RD | Mean value: 31. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8542 | float | RD | Mean value: 32. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8544 | float | RD | Mean value: 33. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8546 | float | RD | Mean value: 34. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8548 | float | RD | Mean value: 35. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8550 | float | RD | Mean value: 36. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8552 | float | RD | Mean value: 37. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8554 | float | RD | Mean value: 38. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8556 | float | RD | Mean value: 39. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8558 | float | RD | Mean value: 40. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 8560 | float | RD | Mean value: 1. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8562 | float | RD | Mean value: 2. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8564 | float | RD | Mean value: 3. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8566 | float | RD | Mean value: 4. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8568 | float | RD | Mean value: 5. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8570 | float | RD | Mean value: 6. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8572 | float | RD | Mean value: 7. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8574 | float | RD | Mean value: 8. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8576 | float | RD | Mean value: 9. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8578 | float | RD | Mean value: 10. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8580 | float | RD | Mean value: 11. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8582 | float | RD | Mean value: 12. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8584 | float | RD | Mean value: 13. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8586 | float | RD | Mean value: 14. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8588 | float | RD | Mean value: 15. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8590 | float | RD | Mean value: 16. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8592 | float | RD | Mean value: 17. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8594 | float | RD | Mean value: 18. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8596 | float | RD | Mean value: 19. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8598 | float | RD | Mean value: 20. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8600 | float | RD | Mean value: 21. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8602 | float | RD | Mean value: 22. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8604 | float | RD | Mean value: 23. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8606 | float | RD | Mean value: 24. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8608 | float | RD | Mean value: 25. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8610 | float | RD | Mean value: 26. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8612 | float | RD | Mean value: 27. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8614 | float | RD | Mean value: 28. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8616 | float | RD | Mean value: 29. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8618 | float | RD | Mean value: 30. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8620 | float | RD | Mean value: 31. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8622 | float | RD | Mean value: 32. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8624 | float | RD | Mean value: 33. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8626 | float | RD | Mean value: 34. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8628 | float | RD | Mean value: 35. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8630 | float | RD | Mean value: 36. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8632 | float | RD | Mean value: 37. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8634 | float | RD | Mean value: 38. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8636 | float | RD | Mean value: 39. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8638 | float | RD | Mean value: 40. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 8640 | float | RD | Mean value: 1. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8642 | float | RD | Mean value: 2. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8644 | float | RD | Mean value: 3. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8646 | float | RD | Mean value: 4. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8648 | float | RD | Mean value: 5. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8650 | float | RD | Mean value: 6. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8652 | float | RD | Mean value: 7. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8654 | float | RD | Mean value: 8. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8656 | float | RD | Mean value: 9. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8658 | float | RD | Mean value: 10. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8660 | float | RD | Mean value: 11. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8662 | float | RD | Mean value: 12. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8664 | float | RD | Mean value: 13. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8666 | float | RD | Mean value: 14. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8668 | float | RD | Mean value: 15. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8670 | float | RD | Mean value: 16. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8672 | float | RD | Mean value: 17. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8674 | float | RD | Mean value: 18. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8676 | float | RD | Mean value: 19. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8678 | float | RD | Mean value: 20. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8680 | float | RD | Mean value: 21. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8682 | float | RD | Mean value: 22. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8684 | float | RD | Mean value: 23. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8686 | float | RD | Mean value: 24. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8688 | float | RD | Mean value: 25. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8690 | float | RD | Mean value: 26. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8692 | float | RD | Mean value: 27. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8694 | float | RD | Mean value: 28. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8696 | float | RD | Mean value: 29. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8698 | float | RD | Mean value: 30. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8700 | float | RD | Mean value: 31. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8702 | float | RD | Mean value: 32. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8704 | float | RD | Mean value: 33. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8706 | float | RD | Mean value: 34. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8708 | float | RD | Mean value: 35. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8710 | float | RD | Mean value: 36. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8712 | float | RD | Mean value: 37. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8714 | float | RD | Mean value: 38. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8716 | float | RD | Mean value: 39. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8718 | float | RD | Mean value: 40. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 8720 | float | RD | Mean value: 1. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8722 | float | RD | Mean value: 2. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8724 | float | RD | Mean value: 3. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8726 | float | RD | Mean value: 4. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8728 | float | RD | Mean value: 5. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8730 | float | RD | Mean value: 6. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8732 | float | RD | Mean value: 7. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8734 | float | RD | Mean value: 8. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8736 | float | RD | Mean value: 9. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8738 | float | RD | Mean value: 10. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8740 | float | RD | Mean value: 11. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8742 | float | RD | Mean value: 12. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8744 | float | RD | Mean value: 13. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8746 | float | RD | Mean value: 14. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8748 | float | RD | Mean value: 15. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8750 | float | RD | Mean value: 16. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8752 | float | RD | Mean value: 17. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8754 | float | RD | Mean value: 18. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8756 | float | RD | Mean value: 19. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8758 | float | RD | Mean value: 20. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8760 | float | RD | Mean value: 21. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8762 | float | RD | Mean value: 22. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8764 | float | RD | Mean value: 23. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8766 | float | RD | Mean value: 24. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8768 | float | RD | Mean value: 25. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8770 | float | RD | Mean value: 26. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8772 | float | RD | Mean value: 27. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8774 | float | RD | Mean value: 28. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8776 | float | RD | Mean value: 29. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8778 | float | RD | Mean value: 30. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8780 | float | RD | Mean value: 31. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8782 | float | RD | Mean value: 32. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8784 | float | RD | Mean value: 33. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8786 | float | RD | Mean value: 34. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8788 | float | RD | Mean value: 35. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8790 | float | RD | Mean value: 36. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8792 | float | RD | Mean value: 37. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8794 | float | RD | Mean value: 38. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8796 | float | RD | Mean value: 39. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8798 | float | RD | Mean value: 40. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 8800 | float | RD | Mean value: 1. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8802 | float | RD | Mean value: 2. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8804 | float | RD | Mean value: 3. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8806 | float | RD | Mean value: 4. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8808 | float | RD | Mean value: 5. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8810 | float | RD | Mean value: 6. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8812 | float | RD | Mean value: 7. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8814 | float | RD | Mean value: 8. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8816 | float | RD | Mean value: 9. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8818 | float | RD | Mean value: 10. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8820 | float | RD | Mean value: 11. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8822 | float | RD | Mean value: 12. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8824 | float | RD | Mean value: 13. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8826 | float | RD | Mean value: 14. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8828 | float | RD | Mean value: 15. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8830 | float | RD | Mean value: 16. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8832 | float | RD | Mean value: 17. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8834 | float | RD | Mean value: 18. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8836 | float | RD | Mean value: 19. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8838 | float | RD | Mean value: 20. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8840 | float | RD | Mean value: 21. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8842 | float | RD | Mean value: 22. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8844 | float | RD | Mean value: 23. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8846 | float | RD | Mean value: 24. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8848 | float | RD | Mean value: 25. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8850 | float | RD | Mean value: 26. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8852 | float | RD | Mean value: 27. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8854 | float | RD | Mean value: 28. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8856 | float | RD | Mean value: 29. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8858 | float | RD | Mean value: 30. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8860 | float | RD | Mean value: 31. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8862 | float | RD | Mean value: 32. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8864 | float | RD | Mean value: 33. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8866 | float | RD | Mean value: 34. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8868 | float | RD | Mean value: 35. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8870 | float | RD | Mean value: 36. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8872 | float | RD | Mean value: 37. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8874 | float | RD | Mean value: 38. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8876 | float | RD | Mean value: 39. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8878 | float | RD | Mean value: 40. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 8880 | float | RD | Mean value: 1. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8882 | float | RD | Mean value: 2. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8884 | float | RD | Mean value: 3. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8886 | float | RD | Mean value: 4. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8888 | float | RD | Mean value: 5. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8890 | float | RD | Mean value: 6. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8892 | float | RD | Mean value: 7. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8894 | float | RD | Mean value: 8. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8896 | float | RD | Mean value: 9. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8898 | float | RD | Mean value: 10. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8900 | float | RD | Mean value: 11. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8902 | float | RD | Mean value: 12. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8904 | float | RD | Mean value: 13. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8906 | float | RD | Mean value: 14. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8908 | float | RD | Mean value: 15. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8910 | float | RD | Mean value: 16. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8912 | float | RD | Mean value: 17. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8914 | float | RD | Mean value: 18. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8916 | float | RD | Mean value: 19. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8918 | float | RD | Mean value: 20. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8920 | float | RD | Mean value: 21. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8922 | float | RD | Mean value: 22. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8924 | float | RD | Mean value: 23. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8926 | float | RD | Mean value: 24. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8928 | float | RD | Mean value: 25. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8930 | float | RD | Mean value: 26. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8932 | float | RD | Mean value: 27. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8934 | float | RD | Mean value: 28. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8936 | float | RD | Mean value: 29. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8938 | float | RD | Mean value: 30. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8940 | float | RD | Mean value: 31. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8942 | float | RD | Mean value: 32. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8944 | float | RD | Mean value: 33. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8946 | float | RD | Mean value: 34. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8948 | float | RD | Mean value: 35. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8950 | float | RD | Mean value: 36. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8952 | float | RD | Mean value: 37. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8954 | float | RD | Mean value: 38. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8956 | float | RD | Mean value: 39. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 8958 | float | RD | Mean value: 40. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 12029 | short (x10) | RD | Mean value: 1. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 12030 | short (x10) | RD | Mean value: 3. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 12031 | short (x10) | RD | Mean value: 5. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 12032 | short (x10) | RD | Mean value: 7. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 12033 | short (x10) | RD | Mean value: 9. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 12034 | short (x10) | RD | Mean value: 11. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 12035 | short (x10) | RD | Mean value: 13. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 12036 | short (x10) | RD | Mean value: 15. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 12037 | short (x10) | RD | Mean value: 17. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 12038 | short (x10) | RD | Mean value: 19. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 12039 | short (x10) | RD | Mean value: 21. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 12040 | short (x10) | RD | Mean value: 23. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 12041 | short (x10) | RD | Mean value: 25. harmonic voltage L1 | V
Moving mean values, fourier analysis | 49 | 12042 | short (x10) | RD | Mean value: 1. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 12043 | short (x10) | RD | Mean value: 3. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 12044 | short (x10) | RD | Mean value: 5. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 12045 | short (x10) | RD | Mean value: 7. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 12046 | short (x10) | RD | Mean value: 9. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 12047 | short (x10) | RD | Mean value: 11. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 12048 | short (x10) | RD | Mean value: 13. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 12049 | short (x10) | RD | Mean value: 15. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 12050 | short (x10) | RD | Mean value: 17. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 12051 | short (x10) | RD | Mean value: 19. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 12052 | short (x10) | RD | Mean value: 21. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 12053 | short (x10) | RD | Mean value: 23. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 12054 | short (x10) | RD | Mean value: 25. harmonic voltage L2 | V
Moving mean values, fourier analysis | 49 | 12055 | short (x10) | RD | Mean value: 1. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 12056 | short (x10) | RD | Mean value: 3. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 12057 | short (x10) | RD | Mean value: 5. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 12058 | short (x10) | RD | Mean value: 7. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 12059 | short (x10) | RD | Mean value: 9. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 12060 | short (x10) | RD | Mean value: 11. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 12061 | short (x10) | RD | Mean value: 13. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 12062 | short (x10) | RD | Mean value: 15. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 12063 | short (x10) | RD | Mean value: 17. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 12064 | short (x10) | RD | Mean value: 19. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 12065 | short (x10) | RD | Mean value: 21. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 12066 | short (x10) | RD | Mean value: 23. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 12067 | short (x10) | RD | Mean value: 25. harmonic voltage L3 | V
Moving mean values, fourier analysis | 49 | 12068 | short (x1000) | RD | Mean value: 1. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 12069 | short (x1000) | RD | Mean value: 3. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 12070 | short (x1000) | RD | Mean value: 5. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 12071 | short (x1000) | RD | Mean value: 7. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 12072 | short (x1000) | RD | Mean value: 9. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 12073 | short (x1000) | RD | Mean value: 11. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 12074 | short (x1000) | RD | Mean value: 13. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 12075 | short (x1000) | RD | Mean value: 15. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 12076 | short (x1000) | RD | Mean value: 17. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 12077 | short (x1000) | RD | Mean value: 19. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 12078 | short (x1000) | RD | Mean value: 21. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 12079 | short (x1000) | RD | Mean value: 23. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 12080 | short (x1000) | RD | Mean value: 25. harmonic current L1 | A
Moving mean values, fourier analysis | 49 | 12081 | short (x1000) | RD | Mean value: 1. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 12082 | short (x1000) | RD | Mean value: 3. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 12083 | short (x1000) | RD | Mean value: 5. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 12084 | short (x1000) | RD | Mean value: 7. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 12085 | short (x1000) | RD | Mean value: 9. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 12086 | short (x1000) | RD | Mean value: 11. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 12087 | short (x1000) | RD | Mean value: 13. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 12088 | short (x1000) | RD | Mean value: 15. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 12089 | short (x1000) | RD | Mean value: 17. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 12090 | short (x1000) | RD | Mean value: 19. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 12091 | short (x1000) | RD | Mean value: 21. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 12092 | short (x1000) | RD | Mean value: 23. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 12093 | short (x1000) | RD | Mean value: 25. harmonic current L2 | A
Moving mean values, fourier analysis | 49 | 12094 | short (x1000) | RD | Mean value: 1. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 12095 | short (x1000) | RD | Mean value: 3. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 12096 | short (x1000) | RD | Mean value: 5. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 12097 | short (x1000) | RD | Mean value: 7. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 12098 | short (x1000) | RD | Mean value: 9. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 12099 | short (x1000) | RD | Mean value: 11. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 12100 | short (x1000) | RD | Mean value: 13. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 12101 | short (x1000) | RD | Mean value: 15. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 12102 | short (x1000) | RD | Mean value: 17. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 12103 | short (x1000) | RD | Mean value: 19. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 12104 | short (x1000) | RD | Mean value: 21. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 12105 | short (x1000) | RD | Mean value: 23. harmonic current L3 | A
Moving mean values, fourier analysis | 49 | 12106 | short (x1000) | RD | Mean value: 25. harmonic current L3 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17000 | float | RD | 41. harmonic voltage L1 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17002 | float | RD | 42. harmonic voltage L1 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17004 | float | RD | 43. harmonic voltage L1 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17006 | float | RD | 44. harmonic voltage L1 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17008 | float | RD | 45. harmonic voltage L1 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17010 | float | RD | 46. harmonic voltage L1 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17012 | float | RD | 47. harmonic voltage L1 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17014 | float | RD | 48. harmonic voltage L1 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17016 | float | RD | 49. harmonic voltage L1 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17018 | float | RD | 50. harmonic voltage L1 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17020 | float | RD | 51. harmonic voltage L1 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17022 | float | RD | 52. harmonic voltage L1 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17024 | float | RD | 53. harmonic voltage L1 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17026 | float | RD | 54. harmonic voltage L1 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17028 | float | RD | 55. harmonic voltage L1 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17030 | float | RD | 56. harmonic voltage L1 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17032 | float | RD | 57. harmonic voltage L1 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17034 | float | RD | 58. harmonic voltage L1 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17036 | float | RD | 59. harmonic voltage L1 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17038 | float | RD | 60. harmonic voltage L1 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17040 | float | RD | 61. harmonic voltage L1 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17042 | float | RD | 62. harmonic voltage L1 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17044 | float | RD | 63. harmonic voltage L1 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17046 | float | RD | 64. harmonic voltage L1 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17048 | float | RD | 65. harmonic voltage L1 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17050 | float | RD | 41. harmonic voltage L2 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17052 | float | RD | 42. harmonic voltage L2 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17054 | float | RD | 43. harmonic voltage L2 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17056 | float | RD | 44. harmonic voltage L2 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17058 | float | RD | 45. harmonic voltage L2 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17060 | float | RD | 46. harmonic voltage L2 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17062 | float | RD | 47. harmonic voltage L2 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17064 | float | RD | 48. harmonic voltage L2 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17066 | float | RD | 49. harmonic voltage L2 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17068 | float | RD | 50. harmonic voltage L2 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17070 | float | RD | 51. harmonic voltage L2 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17072 | float | RD | 52. harmonic voltage L2 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17074 | float | RD | 53. harmonic voltage L2 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17076 | float | RD | 54. harmonic voltage L2 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17078 | float | RD | 55. harmonic voltage L2 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17080 | float | RD | 56. harmonic voltage L2 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17082 | float | RD | 57. harmonic voltage L2 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17084 | float | RD | 58. harmonic voltage L2 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17086 | float | RD | 59. harmonic voltage L2 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17088 | float | RD | 60. harmonic voltage L2 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17090 | float | RD | 61. harmonic voltage L2 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17092 | float | RD | 62. harmonic voltage L2 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17094 | float | RD | 63. harmonic voltage L2 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17096 | float | RD | 64. harmonic voltage L2 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17098 | float | RD | 65. harmonic voltage L2 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17100 | float | RD | 41. harmonic voltage L3 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17102 | float | RD | 42. harmonic voltage L3 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17104 | float | RD | 43. harmonic voltage L3 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17106 | float | RD | 44. harmonic voltage L3 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17108 | float | RD | 45. harmonic voltage L3 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17110 | float | RD | 46. harmonic voltage L3 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17112 | float | RD | 47. harmonic voltage L3 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17114 | float | RD | 48. harmonic voltage L3 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17116 | float | RD | 49. harmonic voltage L3 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17118 | float | RD | 50. harmonic voltage L3 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17120 | float | RD | 51. harmonic voltage L3 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17122 | float | RD | 52. harmonic voltage L3 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17124 | float | RD | 53. harmonic voltage L3 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17126 | float | RD | 54. harmonic voltage L3 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17128 | float | RD | 55. harmonic voltage L3 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17130 | float | RD | 56. harmonic voltage L3 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17132 | float | RD | 57. harmonic voltage L3 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17134 | float | RD | 58. harmonic voltage L3 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17136 | float | RD | 59. harmonic voltage L3 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17138 | float | RD | 60. harmonic voltage L3 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17140 | float | RD | 61. harmonic voltage L3 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17142 | float | RD | 62. harmonic voltage L3 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17144 | float | RD | 63. harmonic voltage L3 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17146 | float | RD | 64. harmonic voltage L3 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17148 | float | RD | 65. harmonic voltage L3 | V
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17150 | float | RD | 41. harmonic current L1 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17152 | float | RD | 42. harmonic current L1 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17154 | float | RD | 43. harmonic current L1 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17156 | float | RD | 44. harmonic current L1 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17158 | float | RD | 45. harmonic current L1 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17160 | float | RD | 46. harmonic current L1 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17162 | float | RD | 47. harmonic current L1 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17164 | float | RD | 48. harmonic current L1 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17166 | float | RD | 49. harmonic current L1 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17168 | float | RD | 50. harmonic current L1 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17170 | float | RD | 51. harmonic current L1 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17172 | float | RD | 52. harmonic current L1 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17174 | float | RD | 53. harmonic current L1 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17176 | float | RD | 54. harmonic current L1 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17178 | float | RD | 55. harmonic current L1 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17180 | float | RD | 56. harmonic current L1 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17182 | float | RD | 57. harmonic current L1 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17184 | float | RD | 58. harmonic current L1 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17186 | float | RD | 59. harmonic current L1 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17188 | float | RD | 60. harmonic current L1 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17190 | float | RD | 61. harmonic current L1 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17192 | float | RD | 62. harmonic current L1 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17194 | float | RD | 63. harmonic current L1 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17196 | float | RD | 64. harmonic current L1 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17198 | float | RD | 65. harmonic current L1 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17200 | float | RD | 41. harmonic current L2 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17202 | float | RD | 42. harmonic current L2 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17204 | float | RD | 43. harmonic current L2 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17206 | float | RD | 44. harmonic current L2 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17208 | float | RD | 45. harmonic current L2 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17210 | float | RD | 46. harmonic current L2 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17212 | float | RD | 47. harmonic current L2 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17214 | float | RD | 48. harmonic current L2 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17216 | float | RD | 49. harmonic current L2 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17218 | float | RD | 50. harmonic current L2 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17220 | float | RD | 51. harmonic current L2 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17222 | float | RD | 52. harmonic current L2 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17224 | float | RD | 53. harmonic current L2 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17226 | float | RD | 54. harmonic current L2 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17228 | float | RD | 55. harmonic current L2 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17230 | float | RD | 56. harmonic current L2 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17232 | float | RD | 57. harmonic current L2 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17234 | float | RD | 58. harmonic current L2 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17236 | float | RD | 59. harmonic current L2 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17238 | float | RD | 60. harmonic current L2 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17240 | float | RD | 61. harmonic current L2 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17242 | float | RD | 62. harmonic current L2 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17244 | float | RD | 63. harmonic current L2 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17246 | float | RD | 64. harmonic current L2 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17248 | float | RD | 65. harmonic current L2 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17250 | float | RD | 41. harmonic current L3 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17252 | float | RD | 42. harmonic current L3 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17254 | float | RD | 43. harmonic current L3 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17256 | float | RD | 44. harmonic current L3 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17258 | float | RD | 45. harmonic current L3 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17260 | float | RD | 46. harmonic current L3 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17262 | float | RD | 47. harmonic current L3 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17264 | float | RD | 48. harmonic current L3 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17266 | float | RD | 49. harmonic current L3 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17268 | float | RD | 50. harmonic current L3 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17270 | float | RD | 51. harmonic current L3 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17272 | float | RD | 52. harmonic current L3 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17274 | float | RD | 53. harmonic current L3 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17276 | float | RD | 54. harmonic current L3 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17278 | float | RD | 55. harmonic current L3 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17280 | float | RD | 56. harmonic current L3 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17282 | float | RD | 57. harmonic current L3 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17284 | float | RD | 58. harmonic current L3 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17286 | float | RD | 59. harmonic current L3 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17288 | float | RD | 60. harmonic current L3 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17290 | float | RD | 61. harmonic current L3 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17292 | float | RD | 62. harmonic current L3 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17294 | float | RD | 63. harmonic current L3 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17296 | float | RD | 64. harmonic current L3 | A
Measured values, extended fourier analysis (41st-65th harmonics) | 51 | 17298 | float | RD | 65. harmonic current L3 | A
Maximum values, extended fourier analysis | 52 | 17600 | float | RD | Max. value: 41. harmonic voltage L1 | V
Maximum values, extended fourier analysis | 52 | 17602 | float | RD | Max. value: 42. harmonic voltage L1 | V
Maximum values, extended fourier analysis | 52 | 17604 | float | RD | Max. value: 43. harmonic voltage L1 | V
Maximum values, extended fourier analysis | 52 | 17606 | float | RD | Max. value: 44. harmonic voltage L1 | V
Maximum values, extended fourier analysis | 52 | 17608 | float | RD | Max. value: 45. harmonic voltage L1 | V
Maximum values, extended fourier analysis | 52 | 17610 | float | RD | Max. value: 46. harmonic voltage L1 | V
Maximum values, extended fourier analysis | 52 | 17612 | float | RD | Max. value: 47. harmonic voltage L1 | V
Maximum values, extended fourier analysis | 52 | 17614 | float | RD | Max. value: 48. harmonic voltage L1 | V
Maximum values, extended fourier analysis | 52 | 17616 | float | RD | Max. value: 49. harmonic voltage L1 | V
Maximum values, extended fourier analysis | 52 | 17618 | float | RD | Max. value: 50. harmonic voltage L1 | V
Maximum values, extended fourier analysis | 52 | 17620 | float | RD | Max. value: 51. harmonic voltage L1 | V
Maximum values, extended fourier analysis | 52 | 17622 | float | RD | Max. value: 52. harmonic voltage L1 | V
Maximum values, extended fourier analysis | 52 | 17624 | float | RD | Max. value: 53. harmonic voltage L1 | V
Maximum values, extended fourier analysis | 52 | 17626 | float | RD | Max. value: 54. harmonic voltage L1 | V
Maximum values, extended fourier analysis | 52 | 17628 | float | RD | Max. value: 55. harmonic voltage L1 | V
Maximum values, extended fourier analysis | 52 | 17630 | float | RD | Max. value: 56. harmonic voltage L1 | V
Maximum values, extended fourier analysis | 52 | 17632 | float | RD | Max. value: 57. harmonic voltage L1 | V
Maximum values, extended fourier analysis | 52 | 17634 | float | RD | Max. value: 58. harmonic voltage L1 | V
Maximum values, extended fourier analysis | 52 | 17636 | float | RD | Max. value: 59. harmonic voltage L1 | V
Maximum values, extended fourier analysis | 52 | 17638 | float | RD | Max. value: 60. harmonic voltage L1 | V
Maximum values, extended fourier analysis | 52 | 17640 | float | RD | Max. value: 61. harmonic voltage L1 | V
Maximum values, extended fourier analysis | 52 | 17642 | float | RD | Max. value: 62. harmonic voltage L1 | V
Maximum values, extended fourier analysis | 52 | 17644 | float | RD | Max. value: 63. harmonic voltage L1 | V
Maximum values, extended fourier analysis | 52 | 17646 | float | RD | Max. value: 64. harmonic voltage L1 | V
Maximum values, extended fourier analysis | 52 | 17648 | float | RD | Max. value: 65. harmonic voltage L1 | V
Maximum values, extended fourier analysis | 52 | 17650 | float | RD | Max. value: 41. harmonic voltage L2 | V
Maximum values, extended fourier analysis | 52 | 17652 | float | RD | Max. value: 42. harmonic current L3 | V
Maximum values, extended fourier analysis | 52 | 17654 | float | RD | Max. value: 43. harmonic current L3 | V
Maximum values, extended fourier analysis | 52 | 17656 | float | RD | Max. value: 44. harmonic current L3 | V
Maximum values, extended fourier analysis | 52 | 17658 | float | RD | Max. value: 45. harmonic current L3 | V
Maximum values, extended fourier analysis | 52 | 17660 | float | RD | Max. value: 46. harmonic current L3 | V
Maximum values, extended fourier analysis | 52 | 17662 | float | RD | Max. value: 47. harmonic current L3 | V
Maximum values, extended fourier analysis | 52 | 17664 | float | RD | Max. value: 48. harmonic current L3 | V
Maximum values, extended fourier analysis | 52 | 17666 | float | RD | Max. value: 49. harmonic current L3 | V
Maximum values, extended fourier analysis | 52 | 17668 | float | RD | Max. value: 50. harmonic current L3 | V
Maximum values, extended fourier analysis | 52 | 17670 | float | RD | Max. value: 51. harmonic current L3 | V
Maximum values, extended fourier analysis | 52 | 17672 | float | RD | Max. value: 52. harmonic current L3 | V
Maximum values, extended fourier analysis | 52 | 17674 | float | RD | Max. value: 53. harmonic current L3 | V
Maximum values, extended fourier analysis | 52 | 17676 | float | RD | Max. value: 54. harmonic current L3 | V
Maximum values, extended fourier analysis | 52 | 17678 | float | RD | Max. value: 55. harmonic current L3 | V
Maximum values, extended fourier analysis | 52 | 17680 | float | RD | Max. value: 56. harmonic current L3 | V
Maximum values, extended fourier analysis | 52 | 17682 | float | RD | Max. value: 57. harmonic current L3 | V
Maximum values, extended fourier analysis | 52 | 17684 | float | RD | Max. value: 58. harmonic current L3 | V
Maximum values, extended fourier analysis | 52 | 17686 | float | RD | Max. value: 59. harmonic current L3 | V
Maximum values, extended fourier analysis | 52 | 17688 | float | RD | Max. value: 60. harmonic current L3 | V
Maximum values, extended fourier analysis | 52 | 17690 | float | RD | Max. value: 61. harmonic current L3 | V
Maximum values, extended fourier analysis | 52 | 17692 | float | RD | Max. value: 62. harmonic current L3 | V
Maximum values, extended fourier analysis | 52 | 17694 | float | RD | Max. value: 63. harmonic current L3 | V
Maximum values, extended fourier analysis | 52 | 17696 | float | RD | Max. value: 64. harmonic current L3 | V
Maximum values, extended fourier analysis | 52 | 17698 | float | RD | Max. value: 65. harmonic current L3 | V
Maximum values, extended fourier analysis | 52 | 17700 | float | RD | Max. value: 41. harmonic voltage L3 | V
Maximum values, extended fourier analysis | 52 | 17702 | float | RD | Max. value: 42. harmonic voltage L3 | V
Maximum values, extended fourier analysis | 52 | 17704 | float | RD | Max. value: 43. harmonic voltage L3 | V
Maximum values, extended fourier analysis | 52 | 17706 | float | RD | Max. value: 44. harmonic voltage L3 | V
Maximum values, extended fourier analysis | 52 | 17708 | float | RD | Max. value: 45. harmonic voltage L3 | V
Maximum values, extended fourier analysis | 52 | 17710 | float | RD | Max. value: 46. harmonic voltage L3 | V
Maximum values, extended fourier analysis | 52 | 17712 | float | RD | Max. value: 47. harmonic voltage L3 | V
Maximum values, extended fourier analysis | 52 | 17714 | float | RD | Max. value: 48. harmonic voltage L3 | V
Maximum values, extended fourier analysis | 52 | 17716 | float | RD | Max. value: 49. harmonic voltage L3 | V
Maximum values, extended fourier analysis | 52 | 17718 | float | RD | Max. value: 50. harmonic voltage L3 | V
Maximum values, extended fourier analysis | 52 | 17720 | float | RD | Max. value: 51. harmonic voltage L3 | V
Maximum values, extended fourier analysis | 52 | 17722 | float | RD | Max. value: 52. harmonic voltage L3 | V
Maximum values, extended fourier analysis | 52 | 17724 | float | RD | Max. value: 53. harmonic voltage L3 | V
Maximum values, extended fourier analysis | 52 | 17726 | float | RD | Max. value: 54. harmonic voltage L3 | V
Maximum values, extended fourier analysis | 52 | 17728 | float | RD | Max. value: 55. harmonic voltage L3 | V
Maximum values, extended fourier analysis | 52 | 17730 | float | RD | Max. value: 56. harmonic voltage L3 | V
Maximum values, extended fourier analysis | 52 | 17732 | float | RD | Max. value: 57. harmonic voltage L3 | V
Maximum values, extended fourier analysis | 52 | 17734 | float | RD | Max. value: 58. harmonic voltage L3 | V
Maximum values, extended fourier analysis | 52 | 17736 | float | RD | Max. value: 59. harmonic voltage L3 | V
Maximum values, extended fourier analysis | 52 | 17738 | float | RD | Max. value: 60. harmonic voltage L3 | V
Maximum values, extended fourier analysis | 52 | 17740 | float | RD | Max. value: 61. harmonic voltage L3 | V
Maximum values, extended fourier analysis | 52 | 17742 | float | RD | Max. value: 62. harmonic voltage L3 | V
Maximum values, extended fourier analysis | 52 | 17744 | float | RD | Max. value: 63. harmonic voltage L3 | V
Maximum values, extended fourier analysis | 52 | 17746 | float | RD | Max. value: 64. harmonic voltage L3 | V
Maximum values, extended fourier analysis | 52 | 17748 | float | RD | Max. value: 65. harmonic voltage L3 | V
Maximum values, extended fourier analysis | 52 | 17750 | float | RD | Max. value: 41. harmonic current L1 | A
Maximum values, extended fourier analysis | 52 | 17752 | float | RD | Max. value: 42. harmonic current L1 | A
Maximum values, extended fourier analysis | 52 | 17754 | float | RD | Max. value: 43. harmonic current L1 | A
Maximum values, extended fourier analysis | 52 | 17756 | float | RD | Max. value: 44. harmonic current L1 | A
Maximum values, extended fourier analysis | 52 | 17758 | float | RD | Max. value: 45. harmonic current L1 | A
Maximum values, extended fourier analysis | 52 | 17760 | float | RD | Max. value: 46. harmonic current L1 | A
Maximum values, extended fourier analysis | 52 | 17762 | float | RD | Max. value: 47. harmonic current L1 | A
Maximum values, extended fourier analysis | 52 | 17764 | float | RD | Max. value: 48. harmonic current L1 | A
Maximum values, extended fourier analysis | 52 | 17766 | float | RD | Max. value: 49. harmonic current L1 | A
Maximum values, extended fourier analysis | 52 | 17768 | float | RD | Max. value: 50. harmonic current L1 | A
Maximum values, extended fourier analysis | 52 | 17770 | float | RD | Max. value: 51. harmonic current L1 | A
Maximum values, extended fourier analysis | 52 | 17772 | float | RD | Max. value: 52. harmonic current L1 | A
Maximum values, extended fourier analysis | 52 | 17774 | float | RD | Max. value: 53. harmonic current L1 | A
Maximum values, extended fourier analysis | 52 | 17776 | float | RD | Max. value: 54. harmonic current L1 | A
Maximum values, extended fourier analysis | 52 | 17778 | float | RD | Max. value: 55. harmonic current L1 | A
Maximum values, extended fourier analysis | 52 | 17780 | float | RD | Max. value: 56. harmonic current L1 | A
Maximum values, extended fourier analysis | 52 | 17782 | float | RD | Max. value: 57. harmonic current L1 | A
Maximum values, extended fourier analysis | 52 | 17784 | float | RD | Max. value: 58. harmonic current L1 | A
Maximum values, extended fourier analysis | 52 | 17786 | float | RD | Max. value: 59. harmonic current L1 | A
Maximum values, extended fourier analysis | 52 | 17788 | float | RD | Max. value: 60. harmonic current L1 | A
Maximum values, extended fourier analysis | 52 | 17790 | float | RD | Max. value: 61. harmonic current L1 | A
Maximum values, extended fourier analysis | 52 | 17792 | float | RD | Max. value: 62. harmonic current L1 | A
Maximum values, extended fourier analysis | 52 | 17794 | float | RD | Max. value: 63. harmonic current L1 | A
Maximum values, extended fourier analysis | 52 | 17796 | float | RD | Max. value: 64. harmonic current L1 | A
Maximum values, extended fourier analysis | 52 | 17798 | float | RD | Max. value: 65. harmonic current L1 | A
Maximum values, extended fourier analysis | 52 | 17800 | float | RD | Max. value: 41. harmonic current L2 | A
Maximum values, extended fourier analysis | 52 | 17802 | float | RD | Max. value: 42. harmonic current L2 | A
Maximum values, extended fourier analysis | 52 | 17804 | float | RD | Max. value: 43. harmonic current L2 | A
Maximum values, extended fourier analysis | 52 | 17806 | float | RD | Max. value: 44. harmonic current L2 | A
Maximum values, extended fourier analysis | 52 | 17808 | float | RD | Max. value: 45. harmonic current L2 | A
Maximum values, extended fourier analysis | 52 | 17810 | float | RD | Max. value: 46. harmonic current L2 | A
Maximum values, extended fourier analysis | 52 | 17812 | float | RD | Max. value: 47. harmonic current L2 | A
Maximum values, extended fourier analysis | 52 | 17814 | float | RD | Max. value: 48. harmonic current L2 | A
Maximum values, extended fourier analysis | 52 | 17816 | float | RD | Max. value: 49. harmonic current L2 | A
Maximum values, extended fourier analysis | 52 | 17818 | float | RD | Max. value: 49. harmonic current L2 | A
Maximum values, extended fourier analysis | 52 | 17820 | float | RD | Max. value: 49. harmonic current L2 | A
Maximum values, extended fourier analysis | 52 | 17822 | float | RD | Max. value: 52. harmonic current L2 | A
Maximum values, extended fourier analysis | 52 | 17824 | float | RD | Max. value: 53. harmonic current L2 | A
Maximum values, extended fourier analysis | 52 | 17826 | float | RD | Max. value: 54. harmonic current L2 | A
Maximum values, extended fourier analysis | 52 | 17828 | float | RD | Max. value: 55. harmonic current L2 | A
Maximum values, extended fourier analysis | 52 | 17830 | float | RD | Max. value: 56. harmonic current L2 | A
Maximum values, extended fourier analysis | 52 | 17832 | float | RD | Max. value: 57. harmonic current L2 | A
Maximum values, extended fourier analysis | 52 | 17834 | float | RD | Max. value: 58. harmonic current L2 | A
Maximum values, extended fourier analysis | 52 | 17836 | float | RD | Max. value: 59. harmonic current L2 | A
Maximum values, extended fourier analysis | 52 | 17838 | float | RD | Max. value: 60. harmonic current L2 | A
Maximum values, extended fourier analysis | 52 | 17840 | float | RD | Max. value: 61. harmonic current L2 | A
Maximum values, extended fourier analysis | 52 | 17842 | float | RD | Max. value: 62. harmonic current L2 | A
Maximum values, extended fourier analysis | 52 | 17844 | float | RD | Max. value: 63. harmonic current L2 | A
Maximum values, extended fourier analysis | 52 | 17846 | float | RD | Max. value: 64. harmonic current L2 | A
Maximum values, extended fourier analysis | 52 | 17848 | float | RD | Max. value: 65. harmonic current L2 | A
Maximum values, extended fourier analysis | 52 | 17850 | float | RD | Max. value: 41. harmonic current L3 | A
Maximum values, extended fourier analysis | 52 | 17852 | float | RD | Max. value: 42. harmonic current L3 | A
Maximum values, extended fourier analysis | 52 | 17854 | float | RD | Max. value: 43. harmonic current L3 | A
Maximum values, extended fourier analysis | 52 | 17856 | float | RD | Max. value: 44. harmonic current L3 | A
Maximum values, extended fourier analysis | 52 | 17858 | float | RD | Max. value: 45. harmonic current L3 | A
Maximum values, extended fourier analysis | 52 | 17860 | float | RD | Max. value: 46. harmonic current L3 | A
Maximum values, extended fourier analysis | 52 | 17862 | float | RD | Max. value: 47. harmonic current L3 | A
Maximum values, extended fourier analysis | 52 | 17864 | float | RD | Max. value: 48. harmonic current L3 | A
Maximum values, extended fourier analysis | 52 | 17866 | float | RD | Max. value: 49. harmonic current L3 | A
Maximum values, extended fourier analysis | 52 | 17868 | float | RD | Max. value: 50. harmonic current L3 | A
Maximum values, extended fourier analysis | 52 | 17870 | float | RD | Max. value: 51. harmonic current L3 | A
Maximum values, extended fourier analysis | 52 | 17872 | float | RD | Max. value: 52. harmonic current L3 | A
Maximum values, extended fourier analysis | 52 | 17874 | float | RD | Max. value: 53. harmonic current L3 | A
Maximum values, extended fourier analysis | 52 | 17876 | float | RD | Max. value: 54. harmonic current L3 | A
Maximum values, extended fourier analysis | 52 | 17878 | float | RD | Max. value: 55. harmonic current L3 | A
Maximum values, extended fourier analysis | 52 | 17880 | float | RD | Max. value: 56. harmonic current L3 | A
Maximum values, extended fourier analysis | 52 | 17882 | float | RD | Max. value: 57. harmonic current L3 | A
Maximum values, extended fourier analysis | 52 | 17884 | float | RD | Max. value: 58. harmonic current L3 | A
Maximum values, extended fourier analysis | 52 | 17886 | float | RD | Max. value: 59. harmonic current L3 | A
Maximum values, extended fourier analysis | 52 | 17888 | float | RD | Max. value: 60. harmonic current L3 | A
Maximum values, extended fourier analysis | 52 | 17890 | float | RD | Max. value: 61. harmonic current L3 | A
Maximum values, extended fourier analysis | 52 | 17892 | float | RD | Max. value: 62. harmonic current L3 | A
Maximum values, extended fourier analysis | 52 | 17894 | float | RD | Max. value: 63. harmonic current L3 | A
Maximum values, extended fourier analysis | 52 | 17896 | float | RD | Max. value: 64. harmonic current L3 | A
Maximum values, extended fourier analysis | 52 | 17898 | float | RD | Max. value: 65. harmonic current L3 | A
Maximum values, timestamp, extended fourier analysis | 53 | 17900 | uint | RD | UTC timestamp: max. value, 41. harmonic voltage L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17902 | uint | RD | UTC timestamp: max. value, 42. harmonic voltage L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17904 | uint | RD | UTC timestamp: max. value, 43. harmonic voltage L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17906 | uint | RD | UTC timestamp: max. value, 44. harmonic voltage L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17908 | uint | RD | UTC timestamp: max. value, 45. harmonic voltage L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17910 | uint | RD | UTC timestamp: max. value, 46. harmonic voltage L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17912 | uint | RD | UTC timestamp: max. value, 47. harmonic voltage L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17914 | uint | RD | UTC timestamp: max. value, 48. harmonic voltage L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17916 | uint | RD | UTC timestamp: max. value, 49. harmonic voltage L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17918 | uint | RD | UTC timestamp: max. value, 50. harmonic voltage L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17920 | uint | RD | UTC timestamp: max. value, 51. harmonic voltage L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17922 | uint | RD | UTC timestamp: max. value, 52. harmonic voltage L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17924 | uint | RD | UTC timestamp: max. value, 53. harmonic voltage L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17926 | uint | RD | UTC timestamp: max. value, 54. harmonic voltage L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17928 | uint | RD | UTC timestamp: max. value, 55. harmonic voltage L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17930 | uint | RD | UTC timestamp: max. value, 56. harmonic voltage L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17932 | uint | RD | UTC timestamp: max. value, 57. harmonic voltage L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17934 | uint | RD | UTC timestamp: max. value, 58. harmonic voltage L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17936 | uint | RD | UTC timestamp: max. value, 59. harmonic voltage L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17938 | uint | RD | UTC timestamp: max. value, 60. harmonic voltage L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17940 | uint | RD | UTC timestamp: max. value, 61. harmonic voltage L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17942 | uint | RD | UTC timestamp: max. value, 62. harmonic voltage L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17944 | uint | RD | UTC timestamp: max. value, 63. harmonic voltage L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17946 | uint | RD | UTC timestamp: max. value, 64. harmonic voltage L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17948 | uint | RD | UTC timestamp: max. value, 65. harmonic voltage L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17950 | uint | RD | UTC timestamp: max. value, 41. harmonic voltage L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17952 | uint | RD | UTC timestamp: max. value, 42. harmonic voltage L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17954 | uint | RD | UTC timestamp: max. value, 43. harmonic voltage L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17956 | uint | RD | UTC timestamp: max. value, 44. harmonic voltage L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17958 | uint | RD | UTC timestamp: max. value, 45. harmonic voltage L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17960 | uint | RD | UTC timestamp: max. value, 46. harmonic voltage L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17962 | uint | RD | UTC timestamp: max. value, 47. harmonic voltage L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17964 | uint | RD | UTC timestamp: max. value, 48. harmonic voltage L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17966 | uint | RD | UTC timestamp: max. value, 49. harmonic voltage L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17968 | uint | RD | UTC timestamp: max. value, 50. harmonic voltage L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17970 | uint | RD | UTC timestamp: max. value, 51. harmonic voltage L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17972 | uint | RD | UTC timestamp: max. value, 52. harmonic voltage L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17974 | uint | RD | UTC timestamp: max. value, 53. harmonic voltage L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17976 | uint | RD | UTC timestamp: max. value, 54. harmonic voltage L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17978 | uint | RD | UTC timestamp: max. value, 55. harmonic voltage L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17980 | uint | RD | UTC timestamp: max. value, 56. harmonic voltage L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17982 | uint | RD | UTC timestamp: max. value, 57. harmonic voltage L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17984 | uint | RD | UTC timestamp: max. value, 58. harmonic voltage L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17986 | uint | RD | UTC timestamp: max. value, 59. harmonic voltage L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17988 | uint | RD | UTC timestamp: max. value, 60. harmonic voltage L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17990 | uint | RD | UTC timestamp: max. value, 61. harmonic voltage L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17992 | uint | RD | UTC timestamp: max. value, 62. harmonic voltage L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17994 | uint | RD | UTC timestamp: max. value, 63. harmonic voltage L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17996 | uint | RD | UTC timestamp: max. value, 64. harmonic voltage L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 17998 | uint | RD | UTC timestamp: max. value, 65. harmonic voltage L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18000 | uint | RD | UTC timestamp: max. value, 41. harmonic voltage L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18002 | uint | RD | UTC timestamp: max. value, 42. harmonic voltage L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18004 | uint | RD | UTC timestamp: max. value, 43. harmonic voltage L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18006 | uint | RD | UTC timestamp: max. value, 44. harmonic voltage L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18008 | uint | RD | UTC timestamp: max. value, 45. harmonic voltage L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18010 | uint | RD | UTC timestamp: max. value, 46. harmonic voltage L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18012 | uint | RD | UTC timestamp: max. value, 47. harmonic voltage L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18014 | uint | RD | UTC timestamp: max. value, 48. harmonic voltage L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18016 | uint | RD | UTC timestamp: max. value, 49. harmonic voltage L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18018 | uint | RD | UTC timestamp: max. value, 50. harmonic voltage L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18020 | uint | RD | UTC timestamp: max. value, 51. harmonic voltage L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18022 | uint | RD | UTC timestamp: max. value, 52. harmonic voltage L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18024 | uint | RD | UTC timestamp: max. value, 53. harmonic voltage L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18026 | uint | RD | UTC timestamp: max. value, 54. harmonic voltage L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18028 | uint | RD | UTC timestamp: max. value, 55. harmonic voltage L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18030 | uint | RD | UTC timestamp: max. value, 56. harmonic voltage L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18032 | uint | RD | UTC timestamp: max. value, 57. harmonic voltage L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18034 | uint | RD | UTC timestamp: max. value, 58. harmonic voltage L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18036 | uint | RD | UTC timestamp: max. value, 59. harmonic voltage L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18038 | uint | RD | UTC timestamp: max. value, 60. harmonic voltage L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18040 | uint | RD | UTC timestamp: max. value, 61. harmonic voltage L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18042 | uint | RD | UTC timestamp: max. value, 62. harmonic voltage L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18044 | uint | RD | UTC timestamp: max. value, 63. harmonic voltage L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18046 | uint | RD | UTC timestamp: max. value, 64. harmonic voltage L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18048 | uint | RD | UTC timestamp: max. value, 65. harmonic voltage L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18050 | uint | RD | UTC timestamp: max. value, 41. harmonic current L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18052 | uint | RD | UTC timestamp: max. value, 42. harmonic current L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18054 | uint | RD | UTC timestamp: max. value, 43. harmonic current L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18056 | uint | RD | UTC timestamp: max. value, 44. harmonic current L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18058 | uint | RD | UTC timestamp: max. value, 45. harmonic current L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18060 | uint | RD | UTC timestamp: max. value, 46. harmonic current L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18062 | uint | RD | UTC timestamp: max. value, 47. harmonic current L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18064 | uint | RD | UTC timestamp: max. value, 48. harmonic current L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18066 | uint | RD | UTC timestamp: max. value, 49. harmonic current L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18068 | uint | RD | UTC timestamp: max. value, 50. harmonic current L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18070 | uint | RD | UTC timestamp: max. value, 51. harmonic current L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18072 | uint | RD | UTC timestamp: max. value, 52. harmonic current L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18074 | uint | RD | UTC timestamp: max. value, 53. harmonic current L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18076 | uint | RD | UTC timestamp: max. value, 54. harmonic current L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18078 | uint | RD | UTC timestamp: max. value, 55. harmonic current L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18080 | uint | RD | UTC timestamp: max. value, 56. harmonic current L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18082 | uint | RD | UTC timestamp: max. value, 57. harmonic current L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18084 | uint | RD | UTC timestamp: max. value, 58. harmonic current L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18086 | uint | RD | UTC timestamp: max. value, 59. harmonic current L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18088 | uint | RD | UTC timestamp: max. value, 60. harmonic current L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18090 | uint | RD | UTC timestamp: max. value, 61. harmonic current L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18092 | uint | RD | UTC timestamp: max. value, 62. harmonic current L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18094 | uint | RD | UTC timestamp: max. value, 63. harmonic current L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18096 | uint | RD | UTC timestamp: max. value, 64. harmonic current L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18098 | uint | RD | UTC timestamp: max. value, 65. harmonic current L1 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18100 | uint | RD | UTC timestamp: max. value, 41. harmonic current L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18102 | uint | RD | UTC timestamp: max. value, 42. harmonic current L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18104 | uint | RD | UTC timestamp: max. value, 43. harmonic current L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18106 | uint | RD | UTC timestamp: max. value, 44. harmonic current L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18108 | uint | RD | UTC timestamp: max. value, 45. harmonic current L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18110 | uint | RD | UTC timestamp: max. value, 46. harmonic current L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18112 | uint | RD | UTC timestamp: max. value, 47. harmonic current L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18114 | uint | RD | UTC timestamp: max. value, 48. harmonic current L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18116 | uint | RD | UTC timestamp: max. value, 49. harmonic current L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18118 | uint | RD | UTC timestamp: max. value, 50. harmonic current L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18120 | uint | RD | UTC timestamp: max. value, 51. harmonic current L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18122 | uint | RD | UTC timestamp: max. value, 52. harmonic current L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18124 | uint | RD | UTC timestamp: max. value, 53. harmonic current L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18126 | uint | RD | UTC timestamp: max. value, 54. harmonic current L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18128 | uint | RD | UTC timestamp: max. value, 55. harmonic current L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18130 | uint | RD | UTC timestamp: max. value, 56. harmonic current L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18132 | uint | RD | UTC timestamp: max. value, 57. harmonic current L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18134 | uint | RD | UTC timestamp: max. value, 58. harmonic current L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18136 | uint | RD | UTC timestamp: max. value, 59. harmonic current L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18138 | uint | RD | UTC timestamp: max. value, 60. harmonic current L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18140 | uint | RD | UTC timestamp: max. value, 61. harmonic current L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18142 | uint | RD | UTC timestamp: max. value, 62. harmonic current L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18144 | uint | RD | UTC timestamp: max. value, 63. harmonic current L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18146 | uint | RD | UTC timestamp: max. value, 64. harmonic current L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18148 | uint | RD | UTC timestamp: max. value, 65. harmonic current L2 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18150 | uint | RD | UTC timestamp: max. value, 41. harmonic current L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18152 | uint | RD | UTC timestamp: max. value, 42. harmonic current L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18154 | uint | RD | UTC timestamp: max. value, 43. harmonic current L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18156 | uint | RD | UTC timestamp: max. value, 44. harmonic current L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18158 | uint | RD | UTC timestamp: max. value, 45. harmonic current L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18160 | uint | RD | UTC timestamp: max. value, 46. harmonic current L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18162 | uint | RD | UTC timestamp: max. value, 47. harmonic current L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18164 | uint | RD | UTC timestamp: max. value, 48. harmonic current L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18166 | uint | RD | UTC timestamp: max. value, 49. harmonic current L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18168 | uint | RD | UTC timestamp: max. value, 50. harmonic current L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18170 | uint | RD | UTC timestamp: max. value, 51. harmonic current L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18172 | uint | RD | UTC timestamp: max. value, 52. harmonic current L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18174 | uint | RD | UTC timestamp: max. value, 53. harmonic current L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18176 | uint | RD | UTC timestamp: max. value, 54. harmonic current L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18178 | uint | RD | UTC timestamp: max. value, 55. harmonic current L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18180 | uint | RD | UTC timestamp: max. value, 56. harmonic current L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18182 | uint | RD | UTC timestamp: max. value, 57. harmonic current L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18184 | uint | RD | UTC timestamp: max. value, 58. harmonic current L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18186 | uint | RD | UTC timestamp: max. value, 59. harmonic current L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18188 | uint | RD | UTC timestamp: max. value, 60. harmonic current L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18190 | uint | RD | UTC timestamp: max. value, 61. harmonic current L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18192 | uint | RD | UTC timestamp: max. value, 62. harmonic current L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18194 | uint | RD | UTC timestamp: max. value, 63. harmonic current L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18196 | uint | RD | UTC timestamp: max. value, 64. harmonic current L3 | s
Maximum values, timestamp, extended fourier analysis | 53 | 18198 | uint | RD | UTC timestamp: max. value, 65. harmonic current L3 | s
Minimum values, extended fourier analysis | 54 | 18200 | float | RD | Min. value, 41. harmonic voltage L1 | V
Minimum values, extended fourier analysis | 54 | 18202 | float | RD | Min. value, 42. harmonic voltage L1 | V
Minimum values, extended fourier analysis | 54 | 18204 | float | RD | Min. value, 43. harmonic voltage L1 | V
Minimum values, extended fourier analysis | 54 | 18206 | float | RD | Min. value, 44. harmonic voltage L1 | V
Minimum values, extended fourier analysis | 54 | 18208 | float | RD | Min. value, 45. harmonic voltage L1 | V
Minimum values, extended fourier analysis | 54 | 18210 | float | RD | Min. value, 46. harmonic voltage L1 | V
Minimum values, extended fourier analysis | 54 | 18212 | float | RD | Min. value, 47. harmonic voltage L1 | V
Minimum values, extended fourier analysis | 54 | 18214 | float | RD | Min. value, 48. harmonic voltage L1 | V
Minimum values, extended fourier analysis | 54 | 18216 | float | RD | Min. value, 49. harmonic voltage L1 | V
Minimum values, extended fourier analysis | 54 | 18218 | float | RD | Min. value, 50. harmonic voltage L1 | V
Minimum values, extended fourier analysis | 54 | 18220 | float | RD | Min. value, 51. harmonic voltage L1 | V
Minimum values, extended fourier analysis | 54 | 18222 | float | RD | Min. value, 52. harmonic voltage L1 | V
Minimum values, extended fourier analysis | 54 | 18224 | float | RD | Min. value, 53. harmonic voltage L1 | V
Minimum values, extended fourier analysis | 54 | 18226 | float | RD | Min. value, 54. harmonic voltage L1 | V
Minimum values, extended fourier analysis | 54 | 18228 | float | RD | Min. value, 55. harmonic voltage L1 | V
Minimum values, extended fourier analysis | 54 | 18230 | float | RD | Min. value, 56. harmonic voltage L1 | V
Minimum values, extended fourier analysis | 54 | 18232 | float | RD | Min. value, 57. harmonic voltage L1 | V
Minimum values, extended fourier analysis | 54 | 18234 | float | RD | Min. value, 58. harmonic voltage L1 | V
Minimum values, extended fourier analysis | 54 | 18236 | float | RD | Min. value, 59. harmonic voltage L1 | V
Minimum values, extended fourier analysis | 54 | 18238 | float | RD | Min. value, 60. harmonic voltage L1 | V
Minimum values, extended fourier analysis | 54 | 18240 | float | RD | Min. value, 61. harmonic voltage L1 | V
Minimum values, extended fourier analysis | 54 | 18242 | float | RD | Min. value, 62. harmonic voltage L1 | V
Minimum values, extended fourier analysis | 54 | 18244 | float | RD | Min. value, 63. harmonic voltage L1 | V
Minimum values, extended fourier analysis | 54 | 18246 | float | RD | Min. value, 64. harmonic voltage L1 | V
Minimum values, extended fourier analysis | 54 | 18248 | float | RD | Min. value, 65. harmonic voltage L1 | V
Minimum values, extended fourier analysis | 54 | 18250 | float | RD | Min. value, 41. harmonic voltage L2 | V
Minimum values, extended fourier analysis | 54 | 18252 | float | RD | Min. value, 42. harmonic voltage L2 | V
Minimum values, extended fourier analysis | 54 | 18254 | float | RD | Min. value, 43. harmonic voltage L2 | V
Minimum values, extended fourier analysis | 54 | 18256 | float | RD | Min. value, 44. harmonic voltage L2 | V
Minimum values, extended fourier analysis | 54 | 18258 | float | RD | Min. value, 45. harmonic voltage L2 | V
Minimum values, extended fourier analysis | 54 | 18260 | float | RD | Min. value, 46. harmonic voltage L2 | V
Minimum values, extended fourier analysis | 54 | 18262 | float | RD | Min. value, 47. harmonic voltage L2 | V
Minimum values, extended fourier analysis | 54 | 18264 | float | RD | Min. value, 48. harmonic voltage L2 | V
Minimum values, extended fourier analysis | 54 | 18266 | float | RD | Min. value, 49. harmonic voltage L2 | V
Minimum values, extended fourier analysis | 54 | 18268 | float | RD | Min. value, 50. harmonic voltage L2 | V
Minimum values, extended fourier analysis | 54 | 18270 | float | RD | Min. value, 51. harmonic voltage L2 | V
Minimum values, extended fourier analysis | 54 | 18272 | float | RD | Min. value, 52. harmonic voltage L2 | V
Minimum values, extended fourier analysis | 54 | 18274 | float | RD | Min. value, 53. harmonic voltage L2 | V
Minimum values, extended fourier analysis | 54 | 18276 | float | RD | Min. value, 54. harmonic voltage L2 | V
Minimum values, extended fourier analysis | 54 | 18278 | float | RD | Min. value, 55. harmonic voltage L2 | V
Minimum values, extended fourier analysis | 54 | 18280 | float | RD | Min. value, 56. harmonic voltage L2 | V
Minimum values, extended fourier analysis | 54 | 18282 | float | RD | Min. value, 57. harmonic voltage L2 | V
Minimum values, extended fourier analysis | 54 | 18284 | float | RD | Min. value, 58. harmonic voltage L2 | V
Minimum values, extended fourier analysis | 54 | 18286 | float | RD | Min. value, 59. harmonic voltage L2 | V
Minimum values, extended fourier analysis | 54 | 18288 | float | RD | Min. value, 60. harmonic voltage L2 | V
Minimum values, extended fourier analysis | 54 | 18290 | float | RD | Min. value, 61. harmonic voltage L2 | V
Minimum values, extended fourier analysis | 54 | 18292 | float | RD | Min. value, 62. harmonic voltage L2 | V
Minimum values, extended fourier analysis | 54 | 18294 | float | RD | Min. value, 63. harmonic voltage L2 | V
Minimum values, extended fourier analysis | 54 | 18296 | float | RD | Min. value, 64. harmonic voltage L2 | V
Minimum values, extended fourier analysis | 54 | 18298 | float | RD | Min. value, 65. harmonic voltage L2 | V
Minimum values, extended fourier analysis | 54 | 18300 | float | RD | Min. value, 41. harmonic voltage L3 | V
Minimum values, extended fourier analysis | 54 | 18302 | float | RD | Min. value, 42. harmonic voltage L3 | V
Minimum values, extended fourier analysis | 54 | 18304 | float | RD | Min. value, 43. harmonic voltage L3 | V
Minimum values, extended fourier analysis | 54 | 18306 | float | RD | Min. value, 44. harmonic voltage L3 | V
Minimum values, extended fourier analysis | 54 | 18308 | float | RD | Min. value, 45. harmonic voltage L3 | V
Minimum values, extended fourier analysis | 54 | 18310 | float | RD | Min. value, 46. harmonic voltage L3 | V
Minimum values, extended fourier analysis | 54 | 18312 | float | RD | Min. value, 47. harmonic voltage L3 | V
Minimum values, extended fourier analysis | 54 | 18314 | float | RD | Min. value, 48. harmonic voltage L3 | V
Minimum values, extended fourier analysis | 54 | 18316 | float | RD | Min. value, 49. harmonic voltage L3 | V
Minimum values, extended fourier analysis | 54 | 18318 | float | RD | Min. value, 50. harmonic voltage L3 | V
Minimum values, extended fourier analysis | 54 | 18320 | float | RD | Min. value, 51. harmonic voltage L3 | V
Minimum values, extended fourier analysis | 54 | 18322 | float | RD | Min. value, 52. harmonic voltage L3 | V
Minimum values, extended fourier analysis | 54 | 18324 | float | RD | Min. value, 53. harmonic voltage L3 | V
Minimum values, extended fourier analysis | 54 | 18326 | float | RD | Min. value, 54. harmonic voltage L3 | V
Minimum values, extended fourier analysis | 54 | 18328 | float | RD | Min. value, 55. harmonic voltage L3 | V
Minimum values, extended fourier analysis | 54 | 18330 | float | RD | Min. value, 56. harmonic voltage L3 | V
Minimum values, extended fourier analysis | 54 | 18332 | float | RD | Min. value, 57. harmonic voltage L3 | V
Minimum values, extended fourier analysis | 54 | 18334 | float | RD | Min. value, 58. harmonic voltage L3 | V
Minimum values, extended fourier analysis | 54 | 18336 | float | RD | Min. value, 59. harmonic voltage L3 | V
Minimum values, extended fourier analysis | 54 | 18338 | float | RD | Min. value, 60. harmonic voltage L3 | V
Minimum values, extended fourier analysis | 54 | 18340 | float | RD | Min. value, 61. harmonic voltage L3 | V
Minimum values, extended fourier analysis | 54 | 18342 | float | RD | Min. value, 62. harmonic voltage L3 | V
Minimum values, extended fourier analysis | 54 | 18344 | float | RD | Min. value, 63. harmonic voltage L3 | V
Minimum values, extended fourier analysis | 54 | 18346 | float | RD | Min. value, 64. harmonic voltage L3 | V
Minimum values, extended fourier analysis | 54 | 18348 | float | RD | Min. value, 65. harmonic voltage L3 | V
Minimum values, timestamp, extended fourier analysis | 55 | 18350 | uint | RD | UTC timestamp: min. value, 41. harmonic voltage L1 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18352 | uint | RD | UTC timestamp: min. value, 42. harmonic voltage L1 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18354 | uint | RD | UTC timestamp: min. value, 43. harmonic voltage L1 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18356 | uint | RD | UTC timestamp: min. value, 44. harmonic voltage L1 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18358 | uint | RD | UTC timestamp: min. value, 45. harmonic voltage L1 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18360 | uint | RD | UTC timestamp: min. value, 46. harmonic voltage L1 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18362 | uint | RD | UTC timestamp: min. value, 47. harmonic voltage L1 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18364 | uint | RD | UTC timestamp: min. value, 48. harmonic voltage L1 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18366 | uint | RD | UTC timestamp: min. value, 49. harmonic voltage L1 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18368 | uint | RD | UTC timestamp: min. value, 50. harmonic voltage L1 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18370 | uint | RD | UTC timestamp: min. value, 51. harmonic voltage L1 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18372 | uint | RD | UTC timestamp: min. value, 52. harmonic voltage L1 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18374 | uint | RD | UTC timestamp: min. value, 53. harmonic voltage L1 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18376 | uint | RD | UTC timestamp: min. value, 54. harmonic voltage L1 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18378 | uint | RD | UTC timestamp: min. value, 55. harmonic voltage L1 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18380 | uint | RD | UTC timestamp: min. value, 56. harmonic voltage L1 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18382 | uint | RD | UTC timestamp: min. value, 57. harmonic voltage L1 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18384 | uint | RD | UTC timestamp: min. value, 58. harmonic voltage L1 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18386 | uint | RD | UTC timestamp: min. value, 59. harmonic voltage L1 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18388 | uint | RD | UTC timestamp: min. value, 60. harmonic voltage L1 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18390 | uint | RD | UTC timestamp: min. value, 61. harmonic voltage L1 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18392 | uint | RD | UTC timestamp: min. value, 62. harmonic voltage L1 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18394 | uint | RD | UTC timestamp: min. value, 63. harmonic voltage L1 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18396 | uint | RD | UTC timestamp: min. value, 64. harmonic voltage L1 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18398 | uint | RD | UTC timestamp: min. value, 65. harmonic voltage L1 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18400 | uint | RD | UTC timestamp: min. value, 41. harmonic voltage L2 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18402 | uint | RD | UTC timestamp: min. value, 42. harmonic voltage L2 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18404 | uint | RD | UTC timestamp: min. value, 43. harmonic voltage L2 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18406 | uint | RD | UTC timestamp: min. value, 44. harmonic voltage L2 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18408 | uint | RD | UTC timestamp: min. value, 45. harmonic voltage L2 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18410 | uint | RD | UTC timestamp: min. value, 46. harmonic voltage L2 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18412 | uint | RD | UTC timestamp: min. value, 47. harmonic voltage L2 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18414 | uint | RD | UTC timestamp: min. value, 48. harmonic voltage L2 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18416 | uint | RD | UTC timestamp: min. value, 49. harmonic voltage L2 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18418 | uint | RD | UTC timestamp: min. value, 50. harmonic voltage L2 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18420 | uint | RD | UTC timestamp: min. value, 51. harmonic voltage L2 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18422 | uint | RD | UTC timestamp: min. value, 52. harmonic voltage L2 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18424 | uint | RD | UTC timestamp: min. value, 53. harmonic voltage L2 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18426 | uint | RD | UTC timestamp: min. value, 54. harmonic voltage L2 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18428 | uint | RD | UTC timestamp: min. value, 55. harmonic voltage L2 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18430 | uint | RD | UTC timestamp: min. value, 56. harmonic voltage L2 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18432 | uint | RD | UTC timestamp: min. value, 57. harmonic voltage L2 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18434 | uint | RD | UTC timestamp: min. value, 58. harmonic voltage L2 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18436 | uint | RD | UTC timestamp: min. value, 59. harmonic voltage L2 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18438 | uint | RD | UTC timestamp: min. value, 60. harmonic voltage L2 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18440 | uint | RD | UTC timestamp: min. value, 61. harmonic voltage L2 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18442 | uint | RD | UTC timestamp: min. value, 62. harmonic voltage L2 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18444 | uint | RD | UTC timestamp: min. value, 63. harmonic voltage L2 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18446 | uint | RD | UTC timestamp: min. value, 64. harmonic voltage L2 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18448 | uint | RD | UTC timestamp: min. value, 65. harmonic voltage L2 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18450 | uint | RD | UTC timestamp: min. value, 41. harmonic voltage L3 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18452 | uint | RD | UTC timestamp: min. value, 42. harmonic voltage L3 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18454 | uint | RD | UTC timestamp: min. value, 43. harmonic voltage L3 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18456 | uint | RD | UTC timestamp: min. value, 44. harmonic voltage L3 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18458 | uint | RD | UTC timestamp: min. value, 45. harmonic voltage L3 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18460 | uint | RD | UTC timestamp: min. value, 46. harmonic voltage L3 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18462 | uint | RD | UTC timestamp: min. value, 47. harmonic voltage L3 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18464 | uint | RD | UTC timestamp: min. value, 48. harmonic voltage L3 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18466 | uint | RD | UTC timestamp: min. value, 49. harmonic voltage L3 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18468 | uint | RD | UTC timestamp: min. value, 50. harmonic voltage L3 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18470 | uint | RD | UTC timestamp: min. value, 51. harmonic voltage L3 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18472 | uint | RD | UTC timestamp: min. value, 52. harmonic voltage L3 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18474 | uint | RD | UTC timestamp: min. value, 53. harmonic voltage L3 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18476 | uint | RD | UTC timestamp: min. value, 54. harmonic voltage L3 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18478 | uint | RD | UTC timestamp: min. value, 55. harmonic voltage L3 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18480 | uint | RD | UTC timestamp: min. value, 56. harmonic voltage L3 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18482 | uint | RD | UTC timestamp: min. value, 57. harmonic voltage L3 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18484 | uint | RD | UTC timestamp: min. value, 58. harmonic voltage L3 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18486 | uint | RD | UTC timestamp: min. value, 59. harmonic voltage L3 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18488 | uint | RD | UTC timestamp: min. value, 60. harmonic voltage L3 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18490 | uint | RD | UTC timestamp: min. value, 61. harmonic voltage L3 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18492 | uint | RD | UTC timestamp: min. value, 62. harmonic voltage L3 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18494 | uint | RD | UTC timestamp: min. value, 63. harmonic voltage L3 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18496 | uint | RD | UTC timestamp: min. value, 64. harmonic voltage L3 | s
Minimum values, timestamp, extended fourier analysis | 55 | 18498 | uint | RD | UTC timestamp: min. value, 65. harmonic voltage L3 | s
Moving mean values, extended fourier analysis | 56 | 17300 | float | RD | Mean value: 41. harmonic voltage L1 | V
Moving mean values, extended fourier analysis | 56 | 17302 | float | RD | Mean value: 42. harmonic voltage L1 | V
Moving mean values, extended fourier analysis | 56 | 17304 | float | RD | Max. value: 43. harmonic voltage L1 | V
Moving mean values, extended fourier analysis | 56 | 17306 | float | RD | Max. value: 44. harmonic voltage L1 | V
Moving mean values, extended fourier analysis | 56 | 17308 | float | RD | Max. value: 45. harmonic voltage L1 | V
Moving mean values, extended fourier analysis | 56 | 17310 | float | RD | Max. value: 46. harmonic voltage L1 | V
Moving mean values, extended fourier analysis | 56 | 17312 | float | RD | Max. value: 47. harmonic voltage L1 | V
Moving mean values, extended fourier analysis | 56 | 17314 | float | RD | Max. value: 48. harmonic voltage L1 | V
Moving mean values, extended fourier analysis | 56 | 17316 | float | RD | Max. value: 49. harmonic voltage L1 | V
Moving mean values, extended fourier analysis | 56 | 17318 | float | RD | Max. value: 50. harmonic voltage L1 | V
Moving mean values, extended fourier analysis | 56 | 17320 | float | RD | Max. value: 51. harmonic voltage L1 | V
Moving mean values, extended fourier analysis | 56 | 17322 | float | RD | Max. value: 52. harmonic voltage L1 | V
Moving mean values, extended fourier analysis | 56 | 17324 | float | RD | Max. value: 53. harmonic voltage L1 | V
Moving mean values, extended fourier analysis | 56 | 17326 | float | RD | Max. value: 54. harmonic voltage L1 | V
Moving mean values, extended fourier analysis | 56 | 17328 | float | RD | Max. value: 55. harmonic voltage L1 | V
Moving mean values, extended fourier analysis | 56 | 17330 | float | RD | Max. value: 56. harmonic voltage L1 | V
Moving mean values, extended fourier analysis | 56 | 17332 | float | RD | Max. value: 57. harmonic voltage L1 | V
Moving mean values, extended fourier analysis | 56 | 17334 | float | RD | Max. value: 58. harmonic voltage L1 | V
Moving mean values, extended fourier analysis | 56 | 17336 | float | RD | Max. value: 59. harmonic voltage L1 | V
Moving mean values, extended fourier analysis | 56 | 17338 | float | RD | Max. value: 60. harmonic voltage L1 | V
Moving mean values, extended fourier analysis | 56 | 17340 | float | RD | Max. value: 61. harmonic voltage L1 | V
Moving mean values, extended fourier analysis | 56 | 17342 | float | RD | Max. value: 62. harmonic voltage L1 | V
Moving mean values, extended fourier analysis | 56 | 17344 | float | RD | Max. value: 63. harmonic voltage L1 | V
Moving mean values, extended fourier analysis | 56 | 17346 | float | RD | Max. value: 64. harmonic voltage L1 | V
Moving mean values, extended fourier analysis | 56 | 17348 | float | RD | Max. value: 65. harmonic voltage L1 | V
Moving mean values, extended fourier analysis | 56 | 17350 | float | RD | Mean value: 41. harmonic voltage L2 | V
Moving mean values, extended fourier analysis | 56 | 17352 | float | RD | Mean value: 42. harmonic voltage L2 | V
Moving mean values, extended fourier analysis | 56 | 17354 | float | RD | Mean value: 43. harmonic voltage L2 | V
Moving mean values, extended fourier analysis | 56 | 17356 | float | RD | Mean value: 44. harmonic voltage L2 | V
Moving mean values, extended fourier analysis | 56 | 17358 | float | RD | Mean value: 45. harmonic voltage L2 | V
Moving mean values, extended fourier analysis | 56 | 17360 | float | RD | Mean value: 46. harmonic voltage L2 | V
Moving mean values, extended fourier analysis | 56 | 17362 | float | RD | Mean value: 47. harmonic voltage L2 | V
Moving mean values, extended fourier analysis | 56 | 17364 | float | RD | Mean value: 48. harmonic voltage L2 | V
Moving mean values, extended fourier analysis | 56 | 17366 | float | RD | Mean value: 49. harmonic voltage L2 | V
Moving mean values, extended fourier analysis | 56 | 17368 | float | RD | Mean value: 50. harmonic voltage L2 | V
Moving mean values, extended fourier analysis | 56 | 17370 | float | RD | Mean value: 51. harmonic voltage L2 | V
Moving mean values, extended fourier analysis | 56 | 17372 | float | RD | Mean value: 52. harmonic voltage L2 | V
Moving mean values, extended fourier analysis | 56 | 17374 | float | RD | Mean value: 53. harmonic voltage L2 | V
Moving mean values, extended fourier analysis | 56 | 17376 | float | RD | Mean value: 54. harmonic voltage L2 | V
Moving mean values, extended fourier analysis | 56 | 17378 | float | RD | Mean value: 55. harmonic voltage L2 | V
Moving mean values, extended fourier analysis | 56 | 17380 | float | RD | Mean value: 56. harmonic voltage L2 | V
Moving mean values, extended fourier analysis | 56 | 17382 | float | RD | Mean value: 57. harmonic voltage L2 | V
Moving mean values, extended fourier analysis | 56 | 17384 | float | RD | Mean value: 58. harmonic voltage L2 | V
Moving mean values, extended fourier analysis | 56 | 17386 | float | RD | Mean value: 59. harmonic voltage L2 | V
Moving mean values, extended fourier analysis | 56 | 17388 | float | RD | Mean value: 60. harmonic voltage L2 | V
Moving mean values, extended fourier analysis | 56 | 17390 | float | RD | Mean value: 61. harmonic voltage L2 | V
Moving mean values, extended fourier analysis | 56 | 17392 | float | RD | Mean value: 62. harmonic voltage L2 | V
Moving mean values, extended fourier analysis | 56 | 17394 | float | RD | Mean value: 63. harmonic voltage L2 | V
Moving mean values, extended fourier analysis | 56 | 17396 | float | RD | Mean value: 64. harmonic voltage L2 | V
Moving mean values, extended fourier analysis | 56 | 17398 | float | RD | Mean value: 65. harmonic voltage L2 | V
Moving mean values, extended fourier analysis | 56 | 17400 | float | RD | Mean value: 41. harmonic voltage L3 | V
Moving mean values, extended fourier analysis | 56 | 17402 | float | RD | Mean value: 42. harmonic voltage L3 | V
Moving mean values, extended fourier analysis | 56 | 17404 | float | RD | Mean value: 43. harmonic voltage L3 | V
Moving mean values, extended fourier analysis | 56 | 17406 | float | RD | Mean value: 44. harmonic voltage L3 | V
Moving mean values, extended fourier analysis | 56 | 17408 | float | RD | Mean value: 45. harmonic voltage L3 | V
Moving mean values, extended fourier analysis | 56 | 17410 | float | RD | Mean value: 46. harmonic voltage L3 | V
Moving mean values, extended fourier analysis | 56 | 17412 | float | RD | Mean value: 47. harmonic voltage L3 | V
Moving mean values, extended fourier analysis | 56 | 17414 | float | RD | Mean value: 48. harmonic voltage L3 | V
Moving mean values, extended fourier analysis | 56 | 17416 | float | RD | Mean value: 49. harmonic voltage L3 | V
Moving mean values, extended fourier analysis | 56 | 17418 | float | RD | Mean value: 50. harmonic voltage L3 | V
Moving mean values, extended fourier analysis | 56 | 17420 | float | RD | Mean value: 51. harmonic voltage L3 | V
Moving mean values, extended fourier analysis | 56 | 17422 | float | RD | Mean value: 52. harmonic voltage L3 | V
Moving mean values, extended fourier analysis | 56 | 17424 | float | RD | Mean value: 53. harmonic voltage L3 | V
Moving mean values, extended fourier analysis | 56 | 17426 | float | RD | Mean value: 54. harmonic voltage L3 | V
Moving mean values, extended fourier analysis | 56 | 17428 | float | RD | Mean value: 55. harmonic voltage L3 | V
Moving mean values, extended fourier analysis | 56 | 17430 | float | RD | Mean value: 56. harmonic voltage L3 | V
Moving mean values, extended fourier analysis | 56 | 17432 | float | RD | Mean value: 57. harmonic voltage L3 | V
Moving mean values, extended fourier analysis | 56 | 17434 | float | RD | Mean value: 58. harmonic voltage L3 | V
Moving mean values, extended fourier analysis | 56 | 17436 | float | RD | Mean value: 59. harmonic voltage L3 | V
Moving mean values, extended fourier analysis | 56 | 17438 | float | RD | Mean value: 60. harmonic voltage L3 | V
Moving mean values, extended fourier analysis | 56 | 17440 | float | RD | Mean value: 61. harmonic voltage L3 | V
Moving mean values, extended fourier analysis | 56 | 17442 | float | RD | Mean value: 62. harmonic voltage L3 | V
Moving mean values, extended fourier analysis | 56 | 17444 | float | RD | Mean value: 63. harmonic voltage L3 | V
Moving mean values, extended fourier analysis | 56 | 17446 | float | RD | Mean value: 64. harmonic voltage L3 | V
Moving mean values, extended fourier analysis | 56 | 17448 | float | RD | Mean value: 65. harmonic voltage L3 | V
Moving mean values, extended fourier analysis | 56 | 17450 | float | RD | Mean value: 41. harmonic current L1 | A
Moving mean values, extended fourier analysis | 56 | 17452 | float | RD | Mean value: 42. harmonic current L1 | A
Moving mean values, extended fourier analysis | 56 | 17454 | float | RD | Mean value: 43. harmonic current L1 | A
Moving mean values, extended fourier analysis | 56 | 17456 | float | RD | Mean value: 44. harmonic current L1 | A
Moving mean values, extended fourier analysis | 56 | 17458 | float | RD | Mean value: 45. harmonic current L1 | A
Moving mean values, extended fourier analysis | 56 | 17460 | float | RD | Mean value: 46. harmonic current L1 | A
Moving mean values, extended fourier analysis | 56 | 17462 | float | RD | Mean value: 47. harmonic current L1 | A
Moving mean values, extended fourier analysis | 56 | 17464 | float | RD | Mean value: 48. harmonic current L1 | A
Moving mean values, extended fourier analysis | 56 | 17466 | float | RD | Mean value: 49. harmonic current L1 | A
Moving mean values, extended fourier analysis | 56 | 17468 | float | RD | Mean value: 50. harmonic current L1 | A
Moving mean values, extended fourier analysis | 56 | 17470 | float | RD | Mean value: 51. harmonic current L1 | A
Moving mean values, extended fourier analysis | 56 | 17472 | float | RD | Mean value: 52. harmonic current L1 | A
Moving mean values, extended fourier analysis | 56 | 17474 | float | RD | Mean value: 53. harmonic current L1 | A
Moving mean values, extended fourier analysis | 56 | 17476 | float | RD | Mean value: 54. harmonic current L1 | A
Moving mean values, extended fourier analysis | 56 | 17478 | float | RD | Mean value: 55. harmonic current L1 | A
Moving mean values, extended fourier analysis | 56 | 17480 | float | RD | Mean value: 56. harmonic current L1 | A
Moving mean values, extended fourier analysis | 56 | 17482 | float | RD | Mean value: 57. harmonic current L1 | A
Moving mean values, extended fourier analysis | 56 | 17484 | float | RD | Mean value: 58. harmonic current L1 | A
Moving mean values, extended fourier analysis | 56 | 17486 | float | RD | Mean value: 59. harmonic current L1 | A
Moving mean values, extended fourier analysis | 56 | 17488 | float | RD | Mean value: 60. harmonic current L1 | A
Moving mean values, extended fourier analysis | 56 | 17490 | float | RD | Mean value: 61. harmonic current L1 | A
Moving mean values, extended fourier analysis | 56 | 17492 | float | RD | Mean value: 62. harmonic current L1 | A
Moving mean values, extended fourier analysis | 56 | 17494 | float | RD | Mean value: 63. harmonic current L1 | A
Moving mean values, extended fourier analysis | 56 | 17496 | float | RD | Mean value: 64. harmonic current L1 | A
Moving mean values, extended fourier analysis | 56 | 17498 | float | RD | Mean value: 65. harmonic current L1 | A
Moving mean values, extended fourier analysis | 56 | 17500 | float | RD | Mean value: 41. harmonic current L2 | A
Moving mean values, extended fourier analysis | 56 | 17502 | float | RD | Mean value: 42. harmonic current L2 | A
Moving mean values, extended fourier analysis | 56 | 17504 | float | RD | Mean value: 43. harmonic current L2 | A
Moving mean values, extended fourier analysis | 56 | 17506 | float | RD | Mean value: 44. harmonic current L2 | A
Moving mean values, extended fourier analysis | 56 | 17508 | float | RD | Mean value: 45. harmonic current L2 | A
Moving mean values, extended fourier analysis | 56 | 17510 | float | RD | Mean value: 46. harmonic current L2 | A
Moving mean values, extended fourier analysis | 56 | 17512 | float | RD | Mean value: 47. harmonic current L2 | A
Moving mean values, extended fourier analysis | 56 | 17514 | float | RD | Mean value: 48. harmonic current L2 | A
Moving mean values, extended fourier analysis | 56 | 17516 | float | RD | Mean value: 49. harmonic current L2 | A
Moving mean values, extended fourier analysis | 56 | 17518 | float | RD | Mean value: 50. harmonic current L2 | A
Moving mean values, extended fourier analysis | 56 | 17520 | float | RD | Mean value: 51. harmonic current L2 | A
Moving mean values, extended fourier analysis | 56 | 17522 | float | RD | Mean value: 52. harmonic current L2 | A
Moving mean values, extended fourier analysis | 56 | 17524 | float | RD | Mean value: 53. harmonic current L2 | A
Moving mean values, extended fourier analysis | 56 | 17526 | float | RD | Mean value: 54. harmonic current L2 | A
Moving mean values, extended fourier analysis | 56 | 17528 | float | RD | Mean value: 55. harmonic current L2 | A
Moving mean values, extended fourier analysis | 56 | 17530 | float | RD | Mean value: 56. harmonic current L2 | A
Moving mean values, extended fourier analysis | 56 | 17532 | float | RD | Mean value: 57. harmonic current L2 | A
Moving mean values, extended fourier analysis | 56 | 17534 | float | RD | Mean value: 58. harmonic current L2 | A
Moving mean values, extended fourier analysis | 56 | 17536 | float | RD | Mean value: 59. harmonic current L2 | A
Moving mean values, extended fourier analysis | 56 | 17538 | float | RD | Mean value: 60. harmonic current L2 | A
Moving mean values, extended fourier analysis | 56 | 17540 | float | RD | Mean value: 61. harmonic current L2 | A
Moving mean values, extended fourier analysis | 56 | 17542 | float | RD | Mean value: 62. harmonic current L2 | A
Moving mean values, extended fourier analysis | 56 | 17544 | float | RD | Mean value: 63. harmonic current L2 | A
Moving mean values, extended fourier analysis | 56 | 17546 | float | RD | Mean value: 64. harmonic current L2 | A
Moving mean values, extended fourier analysis | 56 | 17548 | float | RD | Mean value: 65. harmonic current L2 | A
Moving mean values, extended fourier analysis | 56 | 17550 | float | RD | Mean value: 41. harmonic current L3 | A
Moving mean values, extended fourier analysis | 56 | 17552 | float | RD | Mean value: 42. harmonic current L3 | A
Moving mean values, extended fourier analysis | 56 | 17554 | float | RD | Mean value: 43. harmonic current L3 | A
Moving mean values, extended fourier analysis | 56 | 17556 | float | RD | Mean value: 44. harmonic current L3 | A
Moving mean values, extended fourier analysis | 56 | 17558 | float | RD | Mean value: 45. harmonic current L3 | A
Moving mean values, extended fourier analysis | 56 | 17560 | float | RD | Mean value: 46. harmonic current L3 | A
Moving mean values, extended fourier analysis | 56 | 17562 | float | RD | Mean value: 47. harmonic current L3 | A
Moving mean values, extended fourier analysis | 56 | 17564 | float | RD | Mean value: 48. harmonic current L3 | A
Moving mean values, extended fourier analysis | 56 | 17566 | float | RD | Mean value: 49. harmonic current L3 | A
Moving mean values, extended fourier analysis | 56 | 17568 | float | RD | Mean value: 50. harmonic current L3 | A
Moving mean values, extended fourier analysis | 56 | 17570 | float | RD | Mean value: 51. harmonic current L3 | A
Moving mean values, extended fourier analysis | 56 | 17572 | float | RD | Mean value: 52. harmonic current L3 | A
Moving mean values, extended fourier analysis | 56 | 17574 | float | RD | Mean value: 53. harmonic current L3 | A
Moving mean values, extended fourier analysis | 56 | 17576 | float | RD | Mean value: 54. harmonic current L3 | A
Moving mean values, extended fourier analysis | 56 | 17578 | float | RD | Mean value: 55. harmonic current L3 | A
Moving mean values, extended fourier analysis | 56 | 17580 | float | RD | Mean value: 56. harmonic current L3 | A
Moving mean values, extended fourier analysis | 56 | 17582 | float | RD | Mean value: 57. harmonic current L3 | A
Moving mean values, extended fourier analysis | 56 | 17584 | float | RD | Mean value: 58. harmonic current L3 | A
Moving mean values, extended fourier analysis | 56 | 17586 | float | RD | Mean value: 59. harmonic current L3 | A
Moving mean values, extended fourier analysis | 56 | 17588 | float | RD | Mean value: 60. harmonic current L3 | A
Moving mean values, extended fourier analysis | 56 | 17590 | float | RD | Mean value: 61. harmonic current L3 | A
Moving mean values, extended fourier analysis | 56 | 17592 | float | RD | Mean value: 62. harmonic current L3 | A
Moving mean values, extended fourier analysis | 56 | 17594 | float | RD | Mean value: 63. harmonic current L3 | A
Moving mean values, extended fourier analysis | 56 | 17596 | float | RD | Mean value: 64. harmonic current L3 | A
Moving mean values, extended fourier analysis | 56 | 17598 | float | RD | Mean value: 65. harmonic current L3 | A
Other parameters | 60 | 8 | char | RD/WR | Reset Min/Max values, 1 = Reset
Other parameters | 60 | 9 | char | RD/WR | Reset Energy values, 1 = Reset
Other parameters | 60 | 100 | uint | RD/WR | UTC timestamp for time synchronisation via Modbus (RS485)
Other parameters | 60 | 911 | uint | RD | Serial number
Other parameters | 60 | 20004 | ushort | RD | Firmeware version of the device. Example: '355' means version 3.55
Other parameters | 60 | 20012 | uint | RD/WR | Production number
Other parameters | 60 | 20016 | uint | RD/WR | Article number
Other parameters | 60 | 20047 | ushort | RD/WR | Device type ID: UMG 96-PA=19, UMG 96-PA-MID+=30, UMG 96-PQ-L=32, UMG 96-PQ-L (IT)=34, UMG 96-PQ-L-LP=38 |  | 0 | 65535
Other parameters | 60 | 25000 | string | RD/WR | freely programmable device name. Up to 127 characters
Other parameters | 60 | 25128 | string | RD/WR | Device description. Up to 239 characters
Other parameters | 60 | 31498 | ushort | RD/WR | clock synchronisation validation Interval in hours, set to zero to deactivate | h | 0 | 168
Other parameters | 60 | 31499 | ushort | RD | Validate time synchronization, 0 = valid
Other parameters | 60 | 31500 | ushort | RD/WR | EN60870 Time structure, Millisecond
Other parameters | 60 | 31501 | ushort | RD/WR | EN60870 Time structure, Minutes & Hour
Other parameters | 60 | 31502 | ushort | RD/WR | EN60870 Time structure, Day, Weekday & Month
Other parameters | 60 | 31503 | ushort | RD/WR | EN60870 Time structure, Year
Other parameters | 60 | 32604 | short | RD/WR | enable Modbus Broadcast, device will receive messages with slave address 0, 1 = enable |  | 0 | 1
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21000 | float | RD | 1. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21002 | float | RD | 2. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21004 | float | RD | 3. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21006 | float | RD | 4. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21008 | float | RD | 5. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21010 | float | RD | 6. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21012 | float | RD | 7. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21014 | float | RD | 8. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21016 | float | RD | 9. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21018 | float | RD | 10. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21020 | float | RD | 11. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21022 | float | RD | 12. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21024 | float | RD | 13. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21026 | float | RD | 14. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21028 | float | RD | 15. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21030 | float | RD | 16. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21032 | float | RD | 17. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21034 | float | RD | 18. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21036 | float | RD | 19. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21038 | float | RD | 20. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21040 | float | RD | 21. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21042 | float | RD | 22. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21044 | float | RD | 23. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21046 | float | RD | 24. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21048 | float | RD | 25. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21050 | float | RD | 26. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21052 | float | RD | 27. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21054 | float | RD | 28. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21056 | float | RD | 29. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21058 | float | RD | 30. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21060 | float | RD | 31. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21062 | float | RD | 32. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21064 | float | RD | 33. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21066 | float | RD | 34. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21068 | float | RD | 35. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21070 | float | RD | 36. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21072 | float | RD | 37. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21074 | float | RD | 38. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21076 | float | RD | 39. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21078 | float | RD | 40. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21080 | float | RD | 41. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21082 | float | RD | 42. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21084 | float | RD | 43. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21086 | float | RD | 44. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21088 | float | RD | 45. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21090 | float | RD | 46. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21092 | float | RD | 47. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21094 | float | RD | 48. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21096 | float | RD | 49. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21098 | float | RD | 50. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21100 | float | RD | 51. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21102 | float | RD | 52. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21104 | float | RD | 53. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21106 | float | RD | 54. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21108 | float | RD | 55. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21110 | float | RD | 56. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21112 | float | RD | 57. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21114 | float | RD | 58. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21116 | float | RD | 59. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21118 | float | RD | 60. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21120 | float | RD | 61. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21122 | float | RD | 62. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21124 | float | RD | 63. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21126 | float | RD | 64. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21128 | float | RD | 65. Interharmonics I-L1 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21130 | float | RD | 1. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21132 | float | RD | 2. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21134 | float | RD | 3. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21136 | float | RD | 4. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21138 | float | RD | 5. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21140 | float | RD | 6. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21142 | float | RD | 7. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21144 | float | RD | 8. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21146 | float | RD | 9. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21148 | float | RD | 10. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21150 | float | RD | 11. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21152 | float | RD | 12. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21154 | float | RD | 13. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21156 | float | RD | 14. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21158 | float | RD | 15. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21160 | float | RD | 16. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21162 | float | RD | 17. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21164 | float | RD | 18. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21166 | float | RD | 19. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21168 | float | RD | 20. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21170 | float | RD | 21. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21172 | float | RD | 22. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21174 | float | RD | 23. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21176 | float | RD | 24. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21178 | float | RD | 25. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21180 | float | RD | 26. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21182 | float | RD | 27. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21184 | float | RD | 28. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21186 | float | RD | 29. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21188 | float | RD | 30. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21190 | float | RD | 31. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21192 | float | RD | 32. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21194 | float | RD | 33. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21196 | float | RD | 34. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21198 | float | RD | 35. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21200 | float | RD | 36. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21202 | float | RD | 37. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21204 | float | RD | 38. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21206 | float | RD | 39. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21208 | float | RD | 40. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21210 | float | RD | 41. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21212 | float | RD | 42. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21214 | float | RD | 43. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21216 | float | RD | 44. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21218 | float | RD | 45. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21220 | float | RD | 46. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21222 | float | RD | 47. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21224 | float | RD | 48. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21226 | float | RD | 49. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21228 | float | RD | 50. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21230 | float | RD | 51. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21232 | float | RD | 52. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21234 | float | RD | 53. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21236 | float | RD | 54. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21238 | float | RD | 55. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21240 | float | RD | 56. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21242 | float | RD | 57. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21244 | float | RD | 58. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21246 | float | RD | 59. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21248 | float | RD | 60. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21250 | float | RD | 61. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21252 | float | RD | 62. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21254 | float | RD | 63. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21256 | float | RD | 64. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21258 | float | RD | 65. Interharmonics U-L1 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21260 | float | RD | 1. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21262 | float | RD | 2. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21264 | float | RD | 3. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21266 | float | RD | 4. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21268 | float | RD | 5. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21270 | float | RD | 6. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21272 | float | RD | 7. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21274 | float | RD | 8. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21276 | float | RD | 9. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21278 | float | RD | 10. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21280 | float | RD | 11. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21282 | float | RD | 12. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21284 | float | RD | 13. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21286 | float | RD | 14. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21288 | float | RD | 15. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21290 | float | RD | 16. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21292 | float | RD | 17. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21294 | float | RD | 18. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21296 | float | RD | 19. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21298 | float | RD | 20. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21300 | float | RD | 21. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21302 | float | RD | 22. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21304 | float | RD | 23. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21306 | float | RD | 24. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21308 | float | RD | 25. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21310 | float | RD | 26. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21312 | float | RD | 27. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21314 | float | RD | 28. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21316 | float | RD | 29. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21318 | float | RD | 30. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21320 | float | RD | 31. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21322 | float | RD | 32. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21324 | float | RD | 33. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21326 | float | RD | 34. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21328 | float | RD | 35. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21330 | float | RD | 36. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21332 | float | RD | 37. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21334 | float | RD | 38. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21336 | float | RD | 39. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21338 | float | RD | 40. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21340 | float | RD | 41. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21342 | float | RD | 42. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21344 | float | RD | 43. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21346 | float | RD | 44. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21348 | float | RD | 45. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21350 | float | RD | 46. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21352 | float | RD | 47. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21354 | float | RD | 48. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21356 | float | RD | 49. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21358 | float | RD | 50. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21360 | float | RD | 51. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21362 | float | RD | 52. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21364 | float | RD | 53. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21366 | float | RD | 54. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21368 | float | RD | 55. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21370 | float | RD | 56. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21372 | float | RD | 57. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21374 | float | RD | 58. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21376 | float | RD | 59. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21378 | float | RD | 60. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21380 | float | RD | 61. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21382 | float | RD | 62. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21384 | float | RD | 63. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21386 | float | RD | 64. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21388 | float | RD | 65. Interharmonics I-L2 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21390 | float | RD | 1. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21392 | float | RD | 2. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21394 | float | RD | 3. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21396 | float | RD | 4. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21398 | float | RD | 5. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21400 | float | RD | 6. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21402 | float | RD | 7. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21404 | float | RD | 8. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21406 | float | RD | 9. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21408 | float | RD | 10. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21410 | float | RD | 11. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21412 | float | RD | 12. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21414 | float | RD | 13. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21416 | float | RD | 14. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21418 | float | RD | 15. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21420 | float | RD | 16. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21422 | float | RD | 17. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21424 | float | RD | 18. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21426 | float | RD | 19. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21428 | float | RD | 20. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21430 | float | RD | 21. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21432 | float | RD | 22. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21434 | float | RD | 23. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21436 | float | RD | 24. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21438 | float | RD | 25. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21440 | float | RD | 26. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21442 | float | RD | 27. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21444 | float | RD | 28. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21446 | float | RD | 29. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21448 | float | RD | 30. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21450 | float | RD | 31. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21452 | float | RD | 32. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21454 | float | RD | 33. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21456 | float | RD | 34. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21458 | float | RD | 35. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21460 | float | RD | 36. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21462 | float | RD | 37. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21464 | float | RD | 38. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21466 | float | RD | 39. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21468 | float | RD | 40. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21470 | float | RD | 41. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21472 | float | RD | 42. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21474 | float | RD | 43. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21476 | float | RD | 44. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21478 | float | RD | 45. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21480 | float | RD | 46. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21482 | float | RD | 47. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21484 | float | RD | 48. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21486 | float | RD | 49. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21488 | float | RD | 50. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21490 | float | RD | 51. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21492 | float | RD | 52. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21494 | float | RD | 53. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21496 | float | RD | 54. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21498 | float | RD | 55. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21500 | float | RD | 56. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21502 | float | RD | 57. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21504 | float | RD | 58. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21506 | float | RD | 59. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21508 | float | RD | 60. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21510 | float | RD | 61. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21512 | float | RD | 62. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21514 | float | RD | 63. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21516 | float | RD | 64. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21518 | float | RD | 65. Interharmonics U-L2 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21520 | float | RD | 1. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21522 | float | RD | 2. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21524 | float | RD | 3. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21526 | float | RD | 4. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21528 | float | RD | 5. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21530 | float | RD | 6. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21532 | float | RD | 7. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21534 | float | RD | 8. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21536 | float | RD | 9. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21538 | float | RD | 10. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21540 | float | RD | 11. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21542 | float | RD | 12. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21544 | float | RD | 13. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21546 | float | RD | 14. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21548 | float | RD | 15. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21550 | float | RD | 16. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21552 | float | RD | 17. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21554 | float | RD | 18. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21556 | float | RD | 19. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21558 | float | RD | 20. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21560 | float | RD | 21. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21562 | float | RD | 22. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21564 | float | RD | 23. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21566 | float | RD | 24. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21568 | float | RD | 25. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21570 | float | RD | 26. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21572 | float | RD | 27. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21574 | float | RD | 28. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21576 | float | RD | 29. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21578 | float | RD | 30. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21580 | float | RD | 31. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21582 | float | RD | 32. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21584 | float | RD | 33. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21586 | float | RD | 34. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21588 | float | RD | 35. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21590 | float | RD | 36. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21592 | float | RD | 37. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21594 | float | RD | 38. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21596 | float | RD | 39. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21598 | float | RD | 40. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21600 | float | RD | 41. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21602 | float | RD | 42. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21604 | float | RD | 43. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21606 | float | RD | 44. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21608 | float | RD | 45. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21610 | float | RD | 46. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21612 | float | RD | 47. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21614 | float | RD | 48. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21616 | float | RD | 49. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21618 | float | RD | 50. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21620 | float | RD | 51. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21622 | float | RD | 52. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21624 | float | RD | 53. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21626 | float | RD | 54. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21628 | float | RD | 55. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21630 | float | RD | 56. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21632 | float | RD | 57. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21634 | float | RD | 58. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21636 | float | RD | 59. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21638 | float | RD | 60. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21640 | float | RD | 61. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21642 | float | RD | 62. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21644 | float | RD | 63. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21646 | float | RD | 64. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21648 | float | RD | 65. Interharmonics I-L3 | A
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21650 | float | RD | 1. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21652 | float | RD | 2. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21654 | float | RD | 3. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21656 | float | RD | 4. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21658 | float | RD | 5. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21660 | float | RD | 6. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21662 | float | RD | 7. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21664 | float | RD | 8. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21666 | float | RD | 9. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21668 | float | RD | 10. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21670 | float | RD | 11. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21672 | float | RD | 12. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21674 | float | RD | 13. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21676 | float | RD | 14. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21678 | float | RD | 15. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21680 | float | RD | 16. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21682 | float | RD | 17. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21684 | float | RD | 18. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21686 | float | RD | 19. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21688 | float | RD | 20. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21690 | float | RD | 21. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21692 | float | RD | 22. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21694 | float | RD | 23. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21696 | float | RD | 24. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21698 | float | RD | 25. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21700 | float | RD | 26. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21702 | float | RD | 27. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21704 | float | RD | 28. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21706 | float | RD | 29. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21708 | float | RD | 30. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21710 | float | RD | 31. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21712 | float | RD | 32. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21714 | float | RD | 33. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21716 | float | RD | 34. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21718 | float | RD | 35. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21720 | float | RD | 36. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21722 | float | RD | 37. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21724 | float | RD | 38. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21726 | float | RD | 39. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21728 | float | RD | 40. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21730 | float | RD | 41. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21732 | float | RD | 42. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21734 | float | RD | 43. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21736 | float | RD | 44. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21738 | float | RD | 45. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21740 | float | RD | 46. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21742 | float | RD | 47. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21744 | float | RD | 48. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21746 | float | RD | 49. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21748 | float | RD | 50. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21750 | float | RD | 51. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21752 | float | RD | 52. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21754 | float | RD | 53. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21756 | float | RD | 54. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21758 | float | RD | 55. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21760 | float | RD | 56. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21762 | float | RD | 57. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21764 | float | RD | 58. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21766 | float | RD | 59. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21768 | float | RD | 60. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21770 | float | RD | 61. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21772 | float | RD | 62. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21774 | float | RD | 63. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21776 | float | RD | 64. Interharmonics U-L3 | V
Interharmonics - only with IEC 61000-4-30, class S | 61 | 21778 | float | RD | 65. Interharmonics U-L3 | V
Flicker meas. values - only with IEC 61000-4-30, class S | 62 | 1302 | short | RD/WR | Flicker system (50/60 Hz): 0 = 230V/50Hz, 1 = 120V/50Hz, 2 = 230V/60Hz, 3 = 120V/60Hz |  | 0 | 3
Flicker meas. values - only with IEC 61000-4-30, class S | 62 | 1303 | float | RD | L1 Flicker long therm (2 h)
Flicker meas. values - only with IEC 61000-4-30, class S | 62 | 1305 | float | RD | L2 Flicker long therm (2 h)
Flicker meas. values - only with IEC 61000-4-30, class S | 62 | 1307 | float | RD | L3 Flicker long therm (2 h)
Flicker meas. values - only with IEC 61000-4-30, class S | 62 | 1309 | float | RD | L1 Flicker short therm (10 min)
Flicker meas. values - only with IEC 61000-4-30, class S | 62 | 1311 | float | RD | L2 Flicker short therm (10 min)
Flicker meas. values - only with IEC 61000-4-30, class S | 62 | 1313 | float | RD | L3 Flicker short therm (10 min)
Flicker meas. values - only with IEC 61000-4-30, class S | 62 | 1315 | float | RD | L1 Flicker perception factor
Flicker meas. values - only with IEC 61000-4-30, class S | 62 | 1317 | float | RD | L2 Flicker perception factor
Flicker meas. values - only with IEC 61000-4-30, class S | 62 | 1319 | float | RD | L3 Flicker perception factor
Flicker meas. values - only with IEC 61000-4-30, class S | 62 | 1321 | uint | RD | UTC Starttime of Flicker short term
Flicker meas. values - only with IEC 61000-4-30, class S | 62 | 1323 | uint | RD | UTC Endtime of Flicker short term
Flicker meas. values - only with IEC 61000-4-30, class S | 62 | 1325 | uint | RD | UTC Starttime of Flicker long term
Flicker meas. values - only with IEC 61000-4-30, class S | 62 | 1327 | uint | RD | UTC Endtime of Flicker long term
Other Parameters - only with IEC 61000-4-30, class S | 63 | 1333 | float | RD/WR | Configurable frequency in Hz (float) for ripple control |  | 0 | 3000
Other Parameters - only with IEC 61000-4-30, class S | 63 | 1335 | float | RD | Measured value (float): RMS of ripple control signal UL1 | V
Other Parameters - only with IEC 61000-4-30, class S | 63 | 1337 | float | RD | Measured value (float): RMS of ripple control signal UL2 | V
Other Parameters - only with IEC 61000-4-30, class S | 63 | 1339 | float | RD | Measured value (float): RMS of ripple control signal UL3 | V
Extended address list UMG 96-PQ-L-LP | 70 | 20053 | float | RD/WR | Measured value, current L4 | A | -3.403 e+38 | 3.403 e+38
Extended address list UMG 96-PQ-L-LP | 70 | 20063 | float | RD/WR | 1. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20065 | float | RD/WR | 2. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20067 | float | RD/WR | 3. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20069 | float | RD/WR | 4. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20071 | float | RD/WR | 5. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20073 | float | RD/WR | 6. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20075 | float | RD/WR | 7. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20077 | float | RD/WR | 8. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20079 | float | RD/WR | 9. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20081 | float | RD/WR | 10. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20083 | float | RD/WR | 11. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20085 | float | RD/WR | 12. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20087 | float | RD/WR | 13. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20089 | float | RD/WR | 14. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20091 | float | RD/WR | 15. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20093 | float | RD/WR | 16. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20095 | float | RD/WR | 17. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20097 | float | RD/WR | 18. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20099 | float | RD/WR | 19. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20101 | float | RD/WR | 20. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20103 | float | RD/WR | 21. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20105 | float | RD/WR | 22. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20107 | float | RD/WR | 23. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20109 | float | RD/WR | 24. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20111 | float | RD/WR | 25. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20113 | float | RD/WR | 26. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20115 | float | RD/WR | 27. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20117 | float | RD/WR | 28. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20119 | float | RD/WR | 29. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20121 | float | RD/WR | 30. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20123 | float | RD/WR | 31. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20125 | float | RD/WR | 32. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20127 | float | RD/WR | 33. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20129 | float | RD/WR | 34. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20131 | float | RD/WR | 35. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20133 | float | RD/WR | 36. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20135 | float | RD/WR | 37. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20137 | float | RD/WR | 38. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20139 | float | RD/WR | 39. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20141 | float | RD/WR | 40. harmonic current L4 | A
Extended address list UMG 96-PQ-L-LP | 70 | 20305 | float | RD/WR | mean value, current L4 | A | 0 | 3.403 e+38
Extended address list UMG 96-PQ-L-LP | 70 | 20315 | float | RD/WR | min. value, current L4 | A | 0 | 3.403 e+38
Extended address list UMG 96-PQ-L-LP | 70 | 20325 | float | RD/WR | max. value, current L4 | A | 0 | 3.403 e+38
Extended address list UMG 96-PQ-L-LP | 70 | 20335 | uint | RD/WR | UTC timestamp, min. value, current L4 | s
Extended address list UMG 96-PQ-L-LP | 70 | 20345 | uint | RD/WR | UTC timestamp, max. value, current L4 | s
RCM module: Measured values, type float | 90 | 20053 | float | RD/WR | Measured value, current L4 | A | -3.403 e+38 | 3.403 e+38
RCM module: Measured values, type float | 90 | 20055 | float | RD/WR | RCM module: current RCM1 (I5) | A | -3.403 e+38 | 3.403 e+38
RCM module: Measured values, type float | 90 | 20057 | float | RD/WR | RCM module: current RCM2 (I6) | A | -3.403 e+38 | 3.403 e+38
RCM module: Measured values, type float | 90 | 20059 | float | RD/WR | RCM module: current RCM2 (I6 prop. U6) | V | -3.403 e+38 | 3.403 e+38
RCM module: Measured values, type float | 90 | 20061 | float | RD/WR | RCM module: ext. temperature | GRAD_C | -3.403 e+38 | 3.403 e+38
RCM module: Measured values, type float | 90 | 20303 | float | RD/WR | RCM module: DC power (P=I5*U6) | W | 0 | 3.403 e+38
RCM module: Moving mean values, type float | 91 | 20305 | float | RD/WR | mean value, current L4 | A | 0 | 3.403 e+38
RCM module: Moving mean values, type float | 91 | 20307 | float | RD/WR | RCM module: mean value, current RCM1 (I5) | A | 0 | 3.403 e+38
RCM module: Moving mean values, type float | 91 | 20309 | float | RD/WR | RCM module: mean value, current RCM2 (I6) | A | 0 | 3.403 e+38
RCM module: Moving mean values, type float | 91 | 20311 | float | RD/WR | RCM module: mean value, current RCM2 (I6 prop. U6) | V | 0 | 3.403 e+38
RCM module: Moving mean values, type float | 91 | 20313 | float | RD/WR | RCM module: mean value, ext. temperature | GRAD_C | 0 | 3.403 e+38
RCM module: Minimum values, type float | 92 | 20315 | float | RD/WR | min. value, current L4 | A | 0 | 3.403 e+38
RCM module: Minimum values, type float | 92 | 20317 | float | RD/WR | RCM module: min. value, current RCM1 (I5) | A | 0 | 3.403 e+38
RCM module: Minimum values, type float | 92 | 20319 | float | RD/WR | RCM module: min. value, current RCM2 (I6) | A | 0 | 3.403 e+38
RCM module: Minimum values, type float | 92 | 20321 | float | RD/WR | RCM module: min. value, current RCM2 (I6 prop. U6) | V | 0 | 3.403 e+38
RCM module: Minimum values, type float | 92 | 20323 | float | RD/WR | RCM module: min. value, ext. temperature | GRAD_C | 0 | 3.403 e+38
RCM module: Maximum values, type float | 93 | 20325 | float | RD/WR | max. value, current L4 | A | 0 | 3.403 e+38
RCM module: Maximum values, type float | 93 | 20327 | float | RD/WR | RCM module: max. value, current RCM1 (I5) | A | 0 | 3.403 e+38
RCM module: Maximum values, type float | 93 | 20329 | float | RD/WR | RCM module: max. value, current RCM2 (I6) | A | 0 | 3.403 e+38
RCM module: Maximum values, type float | 93 | 20331 | float | RD/WR | RCM module: max. value, current RCM2 (I6 prop. U6) | V | 0 | 3.403 e+38
RCM module: Maximum values, type float | 93 | 20333 | float | RD/WR | RCM module: max. value, ext. temperature | GRAD_C | 0 | 3.403 e+38
RCM module: Minimum values, time stamp | 94 | 20335 | uint | RD/WR | UTC timestamp, min. value, current L4 | s
RCM module: Minimum values, time stamp | 94 | 20337 | uint | RD/WR | RCM module: UTC timestamp, min. value, current RCM1 (I5) | s
RCM module: Minimum values, time stamp | 94 | 20339 | uint | RD/WR | RCM module: UTC timestamp, min. value, current RCM2 (I6) | s
RCM module: Minimum values, time stamp | 94 | 20341 | uint | RD/WR | RCM module: UTC timestamp, min. value, current RCM2 (I6 prop. U6) | s
RCM module: Minimum values, time stamp | 94 | 20343 | uint | RD/WR | RCM module: UTC timestamp, min. value, ext. temperature | s
RCM module: Maximum values, time stamp | 95 | 20345 | uint | RD/WR | UTC timestamp, max. value, current L4 | s
RCM module: Maximum values, time stamp | 95 | 20347 | uint | RD/WR | RCM module: UTC timestamp, max. value, current RCM1 (I5) | s
RCM module: Maximum values, time stamp | 95 | 20349 | uint | RD/WR | RCM module: UTC timestamp, max. value, current RCM2 (I6) | s
RCM module: Maximum values, time stamp | 95 | 20351 | uint | RD/WR | RCM module: UTC timestamp, max. value, current RCM2 (I6 prop. U6) | s
RCM module: Maximum values, time stamp | 95 | 20353 | uint | RD/WR | RCM module: UTC timestamp, max. value, ext. temperature | s
RCM module: Energy values | 96 | 20355 | double | RD/WR | RCM module: active energy, DC (I5 * U6) | Wh | 0 | 3.403 e+38
RCM module: Energy values | 96 | 20359 | float | RD/WR | RCM module: active energy, DC (I5 * U6) | Wh | 0 | 3.403 e+38
RCM module: Fourier analysis, measured values, float | 98 | 20063 | float | RD/WR | 1. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20065 | float | RD/WR | 2. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20067 | float | RD/WR | 3. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20069 | float | RD/WR | 4. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20071 | float | RD/WR | 5. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20073 | float | RD/WR | 6. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20075 | float | RD/WR | 7. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20077 | float | RD/WR | 8. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20079 | float | RD/WR | 9. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20081 | float | RD/WR | 10. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20083 | float | RD/WR | 11. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20085 | float | RD/WR | 12. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20087 | float | RD/WR | 13. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20089 | float | RD/WR | 14. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20091 | float | RD/WR | 15. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20093 | float | RD/WR | 16. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20095 | float | RD/WR | 17. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20097 | float | RD/WR | 18. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20099 | float | RD/WR | 19. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20101 | float | RD/WR | 20. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20103 | float | RD/WR | 21. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20105 | float | RD/WR | 22. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20107 | float | RD/WR | 23. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20109 | float | RD/WR | 24. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20111 | float | RD/WR | 25. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20113 | float | RD/WR | 26. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20115 | float | RD/WR | 27. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20117 | float | RD/WR | 28. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20119 | float | RD/WR | 29. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20121 | float | RD/WR | 30. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20123 | float | RD/WR | 31. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20125 | float | RD/WR | 32. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20127 | float | RD/WR | 33. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20129 | float | RD/WR | 34. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20131 | float | RD/WR | 35. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20133 | float | RD/WR | 36. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20135 | float | RD/WR | 37. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20137 | float | RD/WR | 38. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20139 | float | RD/WR | 39. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20141 | float | RD/WR | 40. harmonic current L4 | A
RCM module: Fourier analysis, measured values, float | 98 | 20143 | float | RD/WR | RCM module: 1. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20145 | float | RD/WR | RCM module: 2. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20147 | float | RD/WR | RCM module: 3. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20149 | float | RD/WR | RCM module: 4. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20151 | float | RD/WR | RCM module: 5. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20153 | float | RD/WR | RCM module: 6. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20155 | float | RD/WR | RCM module: 7. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20157 | float | RD/WR | RCM module: 8. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20159 | float | RD/WR | RCM module: 9. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20161 | float | RD/WR | RCM module: 10. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20163 | float | RD/WR | RCM module: 11. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20165 | float | RD/WR | RCM module: 12. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20167 | float | RD/WR | RCM module: 13. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20169 | float | RD/WR | RCM module: 14. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20171 | float | RD/WR | RCM module: 15. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20173 | float | RD/WR | RCM module: 16. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20175 | float | RD/WR | RCM module: 17. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20177 | float | RD/WR | RCM module: 18. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20179 | float | RD/WR | RCM module: 19. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20181 | float | RD/WR | RCM module: 20. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20183 | float | RD/WR | RCM module: 21. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20185 | float | RD/WR | RCM module: 22. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20187 | float | RD/WR | RCM module: 23. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20189 | float | RD/WR | RCM module: 24. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20191 | float | RD/WR | RCM module: 25. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20193 | float | RD/WR | RCM module: 26. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20195 | float | RD/WR | RCM module: 27. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20197 | float | RD/WR | RCM module: 28. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20199 | float | RD/WR | RCM module: 29. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20201 | float | RD/WR | RCM module: 30. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20203 | float | RD/WR | RCM module: 31. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20205 | float | RD/WR | RCM module: 32. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20207 | float | RD/WR | RCM module: 33. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20209 | float | RD/WR | RCM module: 34. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20211 | float | RD/WR | RCM module: 35. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20213 | float | RD/WR | RCM module: 36. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20215 | float | RD/WR | RCM module: 37. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20217 | float | RD/WR | RCM module: 38. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20219 | float | RD/WR | RCM module: 39. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20221 | float | RD/WR | RCM module: 40. harmonic current rcm1 (I5) | A
RCM module: Fourier analysis, measured values, float | 98 | 20223 | float | RD/WR | RCM module: 1. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20225 | float | RD/WR | RCM module: 2. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20227 | float | RD/WR | RCM module: 3. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20229 | float | RD/WR | RCM module: 4. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20231 | float | RD/WR | RCM module: 5. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20233 | float | RD/WR | RCM module: 6. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20235 | float | RD/WR | RCM module: 7. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20237 | float | RD/WR | RCM module: 8. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20239 | float | RD/WR | RCM module: 9. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20241 | float | RD/WR | RCM module: 10. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20243 | float | RD/WR | RCM module: 11. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20245 | float | RD/WR | RCM module: 12. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20247 | float | RD/WR | RCM module: 13. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20249 | float | RD/WR | RCM module: 14. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20251 | float | RD/WR | RCM module: 15. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20253 | float | RD/WR | RCM module: 16. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20255 | float | RD/WR | RCM module: 17. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20257 | float | RD/WR | RCM module: 18. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20259 | float | RD/WR | RCM module: 19. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20261 | float | RD/WR | RCM module: 20. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20263 | float | RD/WR | RCM module: 21. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20265 | float | RD/WR | RCM module: 22. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20267 | float | RD/WR | RCM module: 23. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20269 | float | RD/WR | RCM module: 24. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20271 | float | RD/WR | RCM module: 25. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20273 | float | RD/WR | RCM module: 26. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20275 | float | RD/WR | RCM module: 27. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20277 | float | RD/WR | RCM module: 28. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20279 | float | RD/WR | RCM module: 29. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20281 | float | RD/WR | RCM module: 30. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20283 | float | RD/WR | RCM module: 31. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20285 | float | RD/WR | RCM module: 32. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20287 | float | RD/WR | RCM module: 33. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20289 | float | RD/WR | RCM module: 34. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20291 | float | RD/WR | RCM module: 35. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20293 | float | RD/WR | RCM module: 36. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20295 | float | RD/WR | RCM module: 37. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20297 | float | RD/WR | RCM module: 38. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20299 | float | RD/WR | RCM module: 39. harmonic current rcm2 (I6) | A
RCM module: Fourier analysis, measured values, float | 98 | 20301 | float | RD/WR | RCM module: 40. harmonic current rcm2 (I6) | A
RCM module: Other parameters | 99 | 196 | ushort | RD/WR | Firmeware version of the module. Example: '215' means version 2.15
RCM module: Other parameters | 99 | 20051 | ushort | RD/WR | RCM module: RCM1 (I5): CT connection monitoring (AC only): 0=disable; 1=enable |  | 0 | 1
RCM module: Other parameters | 99 | 20052 | ushort | RD/WR | RCM module: RCM2 (I6): CT connection monitoring (AC only): 0=disable; 1=enable |  | 0 | 1
RCM module: Other parameters | 99 | 20393 | ushort | RD | RCM module: RCM1 (I5): status overcurrent, currently: 0= not available; 1= available
RCM module: Other parameters | 99 | 20394 | ushort | RD/WR | RCM module: RCM1 (I5): status overcurrent, previously: 0= not available; 1= available
RCM module: Other parameters | 99 | 20395 | ushort | RD | RCM module: RCM1 (I5): status rcm: Bit 0=1 warning currently available, Bit 1=1 warning previously available, Bit 2=1 alarm currently available, Bit 3=1: alarm previously available, Bit 4=1: CT connection break currently available, Bit 5=1: CT connection break previously available, Bit 6=1: overcurrent currently available, Bit 7=1: overcurrent previously available
RCM module: Other parameters | 99 | 20396 | float | RD | RCM module: RCM1 (I5): current limit (in A) for alarms
RCM module: Other parameters | 99 | 20398 | uint | RD | RCM module: RCM1 (I5): alarm run time (in ms)
RCM module: Other parameters | 99 | 20413 | ushort | RD/WR | RCM module: RCM1 (I5): status overcurrent: Bit 0=1 warning currently available, Bit 1=1 warning previously available, Bit 2=1 alarm currently available, Bit 3=1: alarm previously available, Bit 4=1: CT connection break currently available, Bit 5=1: CT connection break previously available, Bit 6=1: overcurrent currently available, Bit 7=1: overcurrent previously available
RCM module: Other parameters | 99 | 20414 | ushort | RD | RCM module: RCM1 (I5): status (pre-)warning, currently: 0=no warning available; 1=warning available
RCM module: Other parameters | 99 | 20415 | ushort | RD/WR | RCM module: RCM1 (I5): status (pre-)warning, previously: 0=no warning available/delete alarm; 1=warning available
RCM module: Other parameters | 99 | 20416 | ushort | RD | RCM module: RCM1 (I5): status alarm, currently: 0=no warning available; 1=warning available
RCM module: Other parameters | 99 | 20417 | ushort | RD/WR | RCM module: RCM1 (I5): status alarm, previously: 0=no warning available/delete alarm; 1=warning available
RCM module: Other parameters | 99 | 20418 | ushort | RD | RCM module: RCM1 (I5): CT connections (AC only), currently: 0=error-free; 1=error
RCM module: Other parameters | 99 | 20419 | ushort | RD/WR | RCM module: RCM1 (I5): CT connections (AC only), previously: 0=error-free/delete error; 1=error
RCM module: Other parameters | 99 | 20593 | ushort | RD | RCM module: RCM2 (I6): status overcurrent, currently: 0= not available; 1= available
RCM module: Other parameters | 99 | 20594 | ushort | RD/WR | RCM module: RCM2 (I6): status overcurrent, previously: 0= not available; 1= available
RCM module: Other parameters | 99 | 20595 | ushort | RD | RCM module: RCM2 (I6): status: Bit 0=1 warning currently available, Bit 1=1 warning previously available, Bit 2=1 alarm currently available, Bit 3=1: alarm previously available, Bit 4=1: CT connection break currently available, Bit 5=1: CT connection break previously available, Bit 6=1: overcurrent currently available, Bit 7=1: overcurrent previously available
RCM module: Other parameters | 99 | 20596 | float | RD | RCM module: RCM2 (I6): current limit (in A) for alarms
RCM module: Other parameters | 99 | 20598 | uint | RD | RCM module: RCM2 (I6): alarm run time (in ms)
RCM module: Other parameters | 99 | 20613 | ushort | RD/WR | RCM module: RCM2 (I6): status overcurrent: Bit 0=1 warning currently available, Bit 1=1 warning previously available, Bit 2=1 alarm currently available, Bit 3=1: alarm previously available, Bit 4=1: CT connection break currently available, Bit 5=1: CT connection break previously available, Bit 6=1: overcurrent currently available, Bit 7=1: overcurrent previously available
RCM module: Other parameters | 99 | 20614 | ushort | RD | RCM module: RCM2 (I6: status (pre-)warning, currently: 0=no alarm available; 1=alarm available
RCM module: Other parameters | 99 | 20615 | ushort | RD/WR | RCM module: RCM2 (I6): status (pre-)warning, previously: 0=no warning available/delete alarm; 1=warning available
RCM module: Other parameters | 99 | 20616 | ushort | RD | RCM module: RCM2 (I6): status alarm, currently: 0=no alarm available; 1=alarm available
RCM module: Other parameters | 99 | 20617 | ushort | RD/WR | RCM module: RCM2 (I6): status alarm, previously: 0=no alarm available/delete alarm; 1=alarm available
RCM module: Other parameters | 99 | 20618 | ushort | RD | RCM module: RCM2 (I6): CT connections (AC only), currently: 0=error-free; 1=error
RCM module: Other parameters | 99 | 20619 | ushort | RD/WR | RCM module: RCM2 (I6): CT connections (AC only), previously: 0=error-free/delete error; 1=error
RCM module: Other parameters | 99 | 20701 | ushort | RD | RCM module: Warning (3 days - not synchronized) - only MID+
RCM module: Other parameters | 99 | 20702 | ushort | RD | RCM module: Alarm (7 days - not synchronized) - only MID+